## README
FCR Pre-qualification: Mock Frequency Injection Profiles
Frequency profiles to be injected into the resource's control system by the on-site transducer during performance data acquisition. Do not enter measurement data here: the site EMS sends the response to Tensor Cloud at 1-second resolution.
1. Source
Test patterns | Balancing market trading guide ver.10 (2026/07/01), section 2-2 pre-qualification, slide 265 (test b, normal conditions) and slide 267 (test a, abnormal conditions).
Governing rules | Balancing market trading rules, chapter 3, article 22 (verification items) and article 23 (performance data). Article 24 defines the standard patterns the profiles are taken from.
Date | Tensor Energy sets the date with the EMS integrator and the engineer operating the transducer. The area TSO is not involved.
2. The three windows
Why three | Two things have to be shown. Under normal conditions, that the resource responds properly while charging and while not charging. Under abnormal conditions, that it reaches offered capacity across the full span from maximum charge to maximum discharge. No single window shows both.
Window 1 | Test b, staircase, on a charging baseline. Shows droop and deadband while charging.
Window 2 | Test b, same staircase, on a not-charging baseline. Shows droop and deadband while not charging.
Window 3 | Test a, single step, from maximum charge. Establishes offered capacity across the full span.
Spacing | The windows need not be consecutive.
3. Before the run
Recording window | Start the recorder at least one hour before each 30-minute window. With window 1 starting 14:30, recording begins by 13:30. Injection still starts at t=0 of the window. The baseline has to be held through that hour too.
Start time | Enter the date and start time in the yellow cells at the top of each profile sheet. Start times must sit on a 30-minute boundary. Prefilled: window 1 at 14:30, window 2 at 15:30, window 3 at 16:30. Change them to your agreed schedule.
Baseline | Enter the baseline for that window, in kW, in the third yellow cell. It is the value the battery holds flat for the whole window and the hour before it, and it is what the response is measured against. Tensor Energy supplies the three figures. Charging for window 1, not charging for window 2, maximum charge for window 3.
Which column | Pick the frequency column for your area's base frequency, and use the Hokkaido column inside the Hokkaido Electric Power Network area.
Register scaling | Transducer and SCADA points usually take a scaled integer rather than a decimal, commonly Hz×1000, so 60.010 Hz is written as 60010. Scale the chosen frequency column to match your point definition before loading.
Machine setup | Where the resource has LFC and EDC functions, lock them out for the duration of each window.
Pattern changes | Run the profile as supplied here unless Tensor Energy has given you a revised one.
4. Test b (normal conditions), windows 1 and 2
Purpose | Confirms the resource follows its droop curve outside the deadband, on each of the two baselines.
Profile | 30 s at base frequency, then ±0.01, ±0.03, ±0.05, ±0.08, ±0.12 and ±0.16 Hz in that order, positive step first in each pair. Each level is held 120 s, with 30 s at base frequency between levels. The pattern ends at t=1,800 s; a 60 s tail at base frequency is included for recovery.
Deadband | The ±0.01 Hz steps may fall inside the resource's deadband and produce no response. Run the level for its full duration regardless.
How it is scored | In the 30 s after each step, the response, measured from the baseline, must stay within the droop-curve theoretical value ±10% of offered capacity, and at least 90% of evaluation points must be in band per 30-minute window.
5. Test a (abnormal conditions), window 3
Purpose | Confirms the resource reaches its full offered capacity within the required response time, driven from maximum charge so the swing spans charge to discharge.
Profile | 60 s at base frequency, one step down at t=60 s, held until t=660 s, then back to base frequency with a 60 s tail.
Step magnitude | 0.2 Hz, or 0.3 Hz inside the Hokkaido Electric Power Network area.
Response window | Full output must be reached within 30 s, measured from the step.
6. During and after the run
Inject at 1-second intervals and hold each level for its full duration. Do not ramp or smooth between steps. The profile is a staircase and is evaluated as one.
For the duration of each window the transducer replaces the live frequency input.
When the run is finished, remove the injection and confirm the controller is back on the live frequency input before leaving site.

## 1. Test b charging
Window start |  | 2026-10-15 | 14:30
Baseline [kW]
Enter the date in the first yellow cell and the start time in the second, then the baseline this window runs on in the third. The Date, Time and Baseline columns fill in for every row.
Window 1 of 3: test b on a CHARGING baseline. The deviation is the same in both frequency zones. Use the frequency column for the site's base frequency. 1,800 s profile plus a 60 s recovery tail.
Elapsed [s] | Date | Time | Baseline [kW] | Deviation [Hz] | Frequency [Hz] 60 Hz area | Frequency [Hz] 50 Hz area
0 |  |  |  | 0 | 60 | 50
1 |  |  |  | 0 | 60 | 50
2 |  |  |  | 0 | 60 | 50
3 |  |  |  | 0 | 60 | 50
4 |  |  |  | 0 | 60 | 50
5 |  |  |  | 0 | 60 | 50
6 |  |  |  | 0 | 60 | 50
7 |  |  |  | 0 | 60 | 50
8 |  |  |  | 0 | 60 | 50
9 |  |  |  | 0 | 60 | 50
10 |  |  |  | 0 | 60 | 50
11 |  |  |  | 0 | 60 | 50
12 |  |  |  | 0 | 60 | 50
13 |  |  |  | 0 | 60 | 50
14 |  |  |  | 0 | 60 | 50
15 |  |  |  | 0 | 60 | 50
16 |  |  |  | 0 | 60 | 50
17 |  |  |  | 0 | 60 | 50
18 |  |  |  | 0 | 60 | 50
19 |  |  |  | 0 | 60 | 50
20 |  |  |  | 0 | 60 | 50
21 |  |  |  | 0 | 60 | 50
22 |  |  |  | 0 | 60 | 50
23 |  |  |  | 0 | 60 | 50
24 |  |  |  | 0 | 60 | 50
25 |  |  |  | 0 | 60 | 50
26 |  |  |  | 0 | 60 | 50
27 |  |  |  | 0 | 60 | 50
28 |  |  |  | 0 | 60 | 50
29 |  |  |  | 0 | 60 | 50
30 |  |  |  | 0.01 | 60.01 | 50.01
31 |  |  |  | 0.01 | 60.01 | 50.01
32 |  |  |  | 0.01 | 60.01 | 50.01
33 |  |  |  | 0.01 | 60.01 | 50.01
34 |  |  |  | 0.01 | 60.01 | 50.01
35 |  |  |  | 0.01 | 60.01 | 50.01
36 |  |  |  | 0.01 | 60.01 | 50.01
37 |  |  |  | 0.01 | 60.01 | 50.01
38 |  |  |  | 0.01 | 60.01 | 50.01
39 |  |  |  | 0.01 | 60.01 | 50.01
40 |  |  |  | 0.01 | 60.01 | 50.01
41 |  |  |  | 0.01 | 60.01 | 50.01
42 |  |  |  | 0.01 | 60.01 | 50.01
43 |  |  |  | 0.01 | 60.01 | 50.01
44 |  |  |  | 0.01 | 60.01 | 50.01
45 |  |  |  | 0.01 | 60.01 | 50.01
46 |  |  |  | 0.01 | 60.01 | 50.01
47 |  |  |  | 0.01 | 60.01 | 50.01
48 |  |  |  | 0.01 | 60.01 | 50.01
49 |  |  |  | 0.01 | 60.01 | 50.01
50 |  |  |  | 0.01 | 60.01 | 50.01
51 |  |  |  | 0.01 | 60.01 | 50.01
52 |  |  |  | 0.01 | 60.01 | 50.01
53 |  |  |  | 0.01 | 60.01 | 50.01
54 |  |  |  | 0.01 | 60.01 | 50.01
55 |  |  |  | 0.01 | 60.01 | 50.01
56 |  |  |  | 0.01 | 60.01 | 50.01
57 |  |  |  | 0.01 | 60.01 | 50.01
58 |  |  |  | 0.01 | 60.01 | 50.01
59 |  |  |  | 0.01 | 60.01 | 50.01
60 |  |  |  | 0.01 | 60.01 | 50.01
61 |  |  |  | 0.01 | 60.01 | 50.01
62 |  |  |  | 0.01 | 60.01 | 50.01
63 |  |  |  | 0.01 | 60.01 | 50.01
64 |  |  |  | 0.01 | 60.01 | 50.01
65 |  |  |  | 0.01 | 60.01 | 50.01
66 |  |  |  | 0.01 | 60.01 | 50.01
67 |  |  |  | 0.01 | 60.01 | 50.01
68 |  |  |  | 0.01 | 60.01 | 50.01
69 |  |  |  | 0.01 | 60.01 | 50.01
70 |  |  |  | 0.01 | 60.01 | 50.01
71 |  |  |  | 0.01 | 60.01 | 50.01
72 |  |  |  | 0.01 | 60.01 | 50.01
73 |  |  |  | 0.01 | 60.01 | 50.01
74 |  |  |  | 0.01 | 60.01 | 50.01
75 |  |  |  | 0.01 | 60.01 | 50.01
76 |  |  |  | 0.01 | 60.01 | 50.01
77 |  |  |  | 0.01 | 60.01 | 50.01
78 |  |  |  | 0.01 | 60.01 | 50.01
79 |  |  |  | 0.01 | 60.01 | 50.01
80 |  |  |  | 0.01 | 60.01 | 50.01
81 |  |  |  | 0.01 | 60.01 | 50.01
82 |  |  |  | 0.01 | 60.01 | 50.01
83 |  |  |  | 0.01 | 60.01 | 50.01
84 |  |  |  | 0.01 | 60.01 | 50.01
85 |  |  |  | 0.01 | 60.01 | 50.01
86 |  |  |  | 0.01 | 60.01 | 50.01
87 |  |  |  | 0.01 | 60.01 | 50.01
88 |  |  |  | 0.01 | 60.01 | 50.01
89 |  |  |  | 0.01 | 60.01 | 50.01
90 |  |  |  | 0.01 | 60.01 | 50.01
91 |  |  |  | 0.01 | 60.01 | 50.01
92 |  |  |  | 0.01 | 60.01 | 50.01
93 |  |  |  | 0.01 | 60.01 | 50.01
94 |  |  |  | 0.01 | 60.01 | 50.01
95 |  |  |  | 0.01 | 60.01 | 50.01
96 |  |  |  | 0.01 | 60.01 | 50.01
97 |  |  |  | 0.01 | 60.01 | 50.01
98 |  |  |  | 0.01 | 60.01 | 50.01
99 |  |  |  | 0.01 | 60.01 | 50.01
100 |  |  |  | 0.01 | 60.01 | 50.01
101 |  |  |  | 0.01 | 60.01 | 50.01
102 |  |  |  | 0.01 | 60.01 | 50.01
103 |  |  |  | 0.01 | 60.01 | 50.01
104 |  |  |  | 0.01 | 60.01 | 50.01
105 |  |  |  | 0.01 | 60.01 | 50.01
106 |  |  |  | 0.01 | 60.01 | 50.01
107 |  |  |  | 0.01 | 60.01 | 50.01
108 |  |  |  | 0.01 | 60.01 | 50.01
109 |  |  |  | 0.01 | 60.01 | 50.01
110 |  |  |  | 0.01 | 60.01 | 50.01
111 |  |  |  | 0.01 | 60.01 | 50.01
112 |  |  |  | 0.01 | 60.01 | 50.01
113 |  |  |  | 0.01 | 60.01 | 50.01
114 |  |  |  | 0.01 | 60.01 | 50.01
115 |  |  |  | 0.01 | 60.01 | 50.01
116 |  |  |  | 0.01 | 60.01 | 50.01
117 |  |  |  | 0.01 | 60.01 | 50.01
118 |  |  |  | 0.01 | 60.01 | 50.01
119 |  |  |  | 0.01 | 60.01 | 50.01
120 |  |  |  | 0.01 | 60.01 | 50.01
121 |  |  |  | 0.01 | 60.01 | 50.01
122 |  |  |  | 0.01 | 60.01 | 50.01
123 |  |  |  | 0.01 | 60.01 | 50.01
124 |  |  |  | 0.01 | 60.01 | 50.01
125 |  |  |  | 0.01 | 60.01 | 50.01
126 |  |  |  | 0.01 | 60.01 | 50.01
127 |  |  |  | 0.01 | 60.01 | 50.01
128 |  |  |  | 0.01 | 60.01 | 50.01
129 |  |  |  | 0.01 | 60.01 | 50.01
130 |  |  |  | 0.01 | 60.01 | 50.01
131 |  |  |  | 0.01 | 60.01 | 50.01
132 |  |  |  | 0.01 | 60.01 | 50.01
133 |  |  |  | 0.01 | 60.01 | 50.01
134 |  |  |  | 0.01 | 60.01 | 50.01
135 |  |  |  | 0.01 | 60.01 | 50.01
136 |  |  |  | 0.01 | 60.01 | 50.01
137 |  |  |  | 0.01 | 60.01 | 50.01
138 |  |  |  | 0.01 | 60.01 | 50.01
139 |  |  |  | 0.01 | 60.01 | 50.01
140 |  |  |  | 0.01 | 60.01 | 50.01
141 |  |  |  | 0.01 | 60.01 | 50.01
142 |  |  |  | 0.01 | 60.01 | 50.01
143 |  |  |  | 0.01 | 60.01 | 50.01
144 |  |  |  | 0.01 | 60.01 | 50.01
145 |  |  |  | 0.01 | 60.01 | 50.01
146 |  |  |  | 0.01 | 60.01 | 50.01
147 |  |  |  | 0.01 | 60.01 | 50.01
148 |  |  |  | 0.01 | 60.01 | 50.01
149 |  |  |  | 0.01 | 60.01 | 50.01
150 |  |  |  | 0 | 60 | 50
151 |  |  |  | 0 | 60 | 50
152 |  |  |  | 0 | 60 | 50
153 |  |  |  | 0 | 60 | 50
154 |  |  |  | 0 | 60 | 50
155 |  |  |  | 0 | 60 | 50
156 |  |  |  | 0 | 60 | 50
157 |  |  |  | 0 | 60 | 50
158 |  |  |  | 0 | 60 | 50
159 |  |  |  | 0 | 60 | 50
160 |  |  |  | 0 | 60 | 50
161 |  |  |  | 0 | 60 | 50
162 |  |  |  | 0 | 60 | 50
163 |  |  |  | 0 | 60 | 50
164 |  |  |  | 0 | 60 | 50
165 |  |  |  | 0 | 60 | 50
166 |  |  |  | 0 | 60 | 50
167 |  |  |  | 0 | 60 | 50
168 |  |  |  | 0 | 60 | 50
169 |  |  |  | 0 | 60 | 50
170 |  |  |  | 0 | 60 | 50
171 |  |  |  | 0 | 60 | 50
172 |  |  |  | 0 | 60 | 50
173 |  |  |  | 0 | 60 | 50
174 |  |  |  | 0 | 60 | 50
175 |  |  |  | 0 | 60 | 50
176 |  |  |  | 0 | 60 | 50
177 |  |  |  | 0 | 60 | 50
178 |  |  |  | 0 | 60 | 50
179 |  |  |  | 0 | 60 | 50
180 |  |  |  | -0.01 | 59.99 | 49.99
181 |  |  |  | -0.01 | 59.99 | 49.99
182 |  |  |  | -0.01 | 59.99 | 49.99
183 |  |  |  | -0.01 | 59.99 | 49.99
184 |  |  |  | -0.01 | 59.99 | 49.99
185 |  |  |  | -0.01 | 59.99 | 49.99
186 |  |  |  | -0.01 | 59.99 | 49.99
187 |  |  |  | -0.01 | 59.99 | 49.99
188 |  |  |  | -0.01 | 59.99 | 49.99
189 |  |  |  | -0.01 | 59.99 | 49.99
190 |  |  |  | -0.01 | 59.99 | 49.99
191 |  |  |  | -0.01 | 59.99 | 49.99
192 |  |  |  | -0.01 | 59.99 | 49.99
193 |  |  |  | -0.01 | 59.99 | 49.99
194 |  |  |  | -0.01 | 59.99 | 49.99
195 |  |  |  | -0.01 | 59.99 | 49.99
196 |  |  |  | -0.01 | 59.99 | 49.99
197 |  |  |  | -0.01 | 59.99 | 49.99
198 |  |  |  | -0.01 | 59.99 | 49.99
199 |  |  |  | -0.01 | 59.99 | 49.99
200 |  |  |  | -0.01 | 59.99 | 49.99
201 |  |  |  | -0.01 | 59.99 | 49.99
202 |  |  |  | -0.01 | 59.99 | 49.99
203 |  |  |  | -0.01 | 59.99 | 49.99
204 |  |  |  | -0.01 | 59.99 | 49.99
205 |  |  |  | -0.01 | 59.99 | 49.99
206 |  |  |  | -0.01 | 59.99 | 49.99
207 |  |  |  | -0.01 | 59.99 | 49.99
208 |  |  |  | -0.01 | 59.99 | 49.99
209 |  |  |  | -0.01 | 59.99 | 49.99
210 |  |  |  | -0.01 | 59.99 | 49.99
211 |  |  |  | -0.01 | 59.99 | 49.99
212 |  |  |  | -0.01 | 59.99 | 49.99
213 |  |  |  | -0.01 | 59.99 | 49.99
214 |  |  |  | -0.01 | 59.99 | 49.99
215 |  |  |  | -0.01 | 59.99 | 49.99
216 |  |  |  | -0.01 | 59.99 | 49.99
217 |  |  |  | -0.01 | 59.99 | 49.99
218 |  |  |  | -0.01 | 59.99 | 49.99
219 |  |  |  | -0.01 | 59.99 | 49.99
220 |  |  |  | -0.01 | 59.99 | 49.99
221 |  |  |  | -0.01 | 59.99 | 49.99
222 |  |  |  | -0.01 | 59.99 | 49.99
223 |  |  |  | -0.01 | 59.99 | 49.99
224 |  |  |  | -0.01 | 59.99 | 49.99
225 |  |  |  | -0.01 | 59.99 | 49.99
226 |  |  |  | -0.01 | 59.99 | 49.99
227 |  |  |  | -0.01 | 59.99 | 49.99
228 |  |  |  | -0.01 | 59.99 | 49.99
229 |  |  |  | -0.01 | 59.99 | 49.99
230 |  |  |  | -0.01 | 59.99 | 49.99
231 |  |  |  | -0.01 | 59.99 | 49.99
232 |  |  |  | -0.01 | 59.99 | 49.99
233 |  |  |  | -0.01 | 59.99 | 49.99
234 |  |  |  | -0.01 | 59.99 | 49.99
235 |  |  |  | -0.01 | 59.99 | 49.99
236 |  |  |  | -0.01 | 59.99 | 49.99
237 |  |  |  | -0.01 | 59.99 | 49.99
238 |  |  |  | -0.01 | 59.99 | 49.99
239 |  |  |  | -0.01 | 59.99 | 49.99
240 |  |  |  | -0.01 | 59.99 | 49.99
241 |  |  |  | -0.01 | 59.99 | 49.99
242 |  |  |  | -0.01 | 59.99 | 49.99
243 |  |  |  | -0.01 | 59.99 | 49.99
244 |  |  |  | -0.01 | 59.99 | 49.99
245 |  |  |  | -0.01 | 59.99 | 49.99
246 |  |  |  | -0.01 | 59.99 | 49.99
247 |  |  |  | -0.01 | 59.99 | 49.99
248 |  |  |  | -0.01 | 59.99 | 49.99
249 |  |  |  | -0.01 | 59.99 | 49.99
250 |  |  |  | -0.01 | 59.99 | 49.99
251 |  |  |  | -0.01 | 59.99 | 49.99
252 |  |  |  | -0.01 | 59.99 | 49.99
253 |  |  |  | -0.01 | 59.99 | 49.99
254 |  |  |  | -0.01 | 59.99 | 49.99
255 |  |  |  | -0.01 | 59.99 | 49.99
256 |  |  |  | -0.01 | 59.99 | 49.99
257 |  |  |  | -0.01 | 59.99 | 49.99
258 |  |  |  | -0.01 | 59.99 | 49.99
259 |  |  |  | -0.01 | 59.99 | 49.99
260 |  |  |  | -0.01 | 59.99 | 49.99
261 |  |  |  | -0.01 | 59.99 | 49.99
262 |  |  |  | -0.01 | 59.99 | 49.99
263 |  |  |  | -0.01 | 59.99 | 49.99
264 |  |  |  | -0.01 | 59.99 | 49.99
265 |  |  |  | -0.01 | 59.99 | 49.99
266 |  |  |  | -0.01 | 59.99 | 49.99
267 |  |  |  | -0.01 | 59.99 | 49.99
268 |  |  |  | -0.01 | 59.99 | 49.99
269 |  |  |  | -0.01 | 59.99 | 49.99
270 |  |  |  | -0.01 | 59.99 | 49.99
271 |  |  |  | -0.01 | 59.99 | 49.99
272 |  |  |  | -0.01 | 59.99 | 49.99
273 |  |  |  | -0.01 | 59.99 | 49.99
274 |  |  |  | -0.01 | 59.99 | 49.99
275 |  |  |  | -0.01 | 59.99 | 49.99
276 |  |  |  | -0.01 | 59.99 | 49.99
277 |  |  |  | -0.01 | 59.99 | 49.99
278 |  |  |  | -0.01 | 59.99 | 49.99
279 |  |  |  | -0.01 | 59.99 | 49.99
280 |  |  |  | -0.01 | 59.99 | 49.99
281 |  |  |  | -0.01 | 59.99 | 49.99
282 |  |  |  | -0.01 | 59.99 | 49.99
283 |  |  |  | -0.01 | 59.99 | 49.99
284 |  |  |  | -0.01 | 59.99 | 49.99
285 |  |  |  | -0.01 | 59.99 | 49.99
286 |  |  |  | -0.01 | 59.99 | 49.99
287 |  |  |  | -0.01 | 59.99 | 49.99
288 |  |  |  | -0.01 | 59.99 | 49.99
289 |  |  |  | -0.01 | 59.99 | 49.99
290 |  |  |  | -0.01 | 59.99 | 49.99
291 |  |  |  | -0.01 | 59.99 | 49.99
292 |  |  |  | -0.01 | 59.99 | 49.99
293 |  |  |  | -0.01 | 59.99 | 49.99
294 |  |  |  | -0.01 | 59.99 | 49.99
295 |  |  |  | -0.01 | 59.99 | 49.99
296 |  |  |  | -0.01 | 59.99 | 49.99
297 |  |  |  | -0.01 | 59.99 | 49.99
298 |  |  |  | -0.01 | 59.99 | 49.99
299 |  |  |  | -0.01 | 59.99 | 49.99
300 |  |  |  | 0 | 60 | 50
301 |  |  |  | 0 | 60 | 50
302 |  |  |  | 0 | 60 | 50
303 |  |  |  | 0 | 60 | 50
304 |  |  |  | 0 | 60 | 50
305 |  |  |  | 0 | 60 | 50
306 |  |  |  | 0 | 60 | 50
307 |  |  |  | 0 | 60 | 50
308 |  |  |  | 0 | 60 | 50
309 |  |  |  | 0 | 60 | 50
310 |  |  |  | 0 | 60 | 50
311 |  |  |  | 0 | 60 | 50
312 |  |  |  | 0 | 60 | 50
313 |  |  |  | 0 | 60 | 50
314 |  |  |  | 0 | 60 | 50
315 |  |  |  | 0 | 60 | 50
316 |  |  |  | 0 | 60 | 50
317 |  |  |  | 0 | 60 | 50
318 |  |  |  | 0 | 60 | 50
319 |  |  |  | 0 | 60 | 50
320 |  |  |  | 0 | 60 | 50
321 |  |  |  | 0 | 60 | 50
322 |  |  |  | 0 | 60 | 50
323 |  |  |  | 0 | 60 | 50
324 |  |  |  | 0 | 60 | 50
325 |  |  |  | 0 | 60 | 50
326 |  |  |  | 0 | 60 | 50
327 |  |  |  | 0 | 60 | 50
328 |  |  |  | 0 | 60 | 50
329 |  |  |  | 0 | 60 | 50
330 |  |  |  | 0.03 | 60.03 | 50.03
331 |  |  |  | 0.03 | 60.03 | 50.03
332 |  |  |  | 0.03 | 60.03 | 50.03
333 |  |  |  | 0.03 | 60.03 | 50.03
334 |  |  |  | 0.03 | 60.03 | 50.03
335 |  |  |  | 0.03 | 60.03 | 50.03
336 |  |  |  | 0.03 | 60.03 | 50.03
337 |  |  |  | 0.03 | 60.03 | 50.03
338 |  |  |  | 0.03 | 60.03 | 50.03
339 |  |  |  | 0.03 | 60.03 | 50.03
340 |  |  |  | 0.03 | 60.03 | 50.03
341 |  |  |  | 0.03 | 60.03 | 50.03
342 |  |  |  | 0.03 | 60.03 | 50.03
343 |  |  |  | 0.03 | 60.03 | 50.03
344 |  |  |  | 0.03 | 60.03 | 50.03
345 |  |  |  | 0.03 | 60.03 | 50.03
346 |  |  |  | 0.03 | 60.03 | 50.03
347 |  |  |  | 0.03 | 60.03 | 50.03
348 |  |  |  | 0.03 | 60.03 | 50.03
349 |  |  |  | 0.03 | 60.03 | 50.03
350 |  |  |  | 0.03 | 60.03 | 50.03
351 |  |  |  | 0.03 | 60.03 | 50.03
352 |  |  |  | 0.03 | 60.03 | 50.03
353 |  |  |  | 0.03 | 60.03 | 50.03
354 |  |  |  | 0.03 | 60.03 | 50.03
355 |  |  |  | 0.03 | 60.03 | 50.03
356 |  |  |  | 0.03 | 60.03 | 50.03
357 |  |  |  | 0.03 | 60.03 | 50.03
358 |  |  |  | 0.03 | 60.03 | 50.03
359 |  |  |  | 0.03 | 60.03 | 50.03
360 |  |  |  | 0.03 | 60.03 | 50.03
361 |  |  |  | 0.03 | 60.03 | 50.03
362 |  |  |  | 0.03 | 60.03 | 50.03
363 |  |  |  | 0.03 | 60.03 | 50.03
364 |  |  |  | 0.03 | 60.03 | 50.03
365 |  |  |  | 0.03 | 60.03 | 50.03
366 |  |  |  | 0.03 | 60.03 | 50.03
367 |  |  |  | 0.03 | 60.03 | 50.03
368 |  |  |  | 0.03 | 60.03 | 50.03
369 |  |  |  | 0.03 | 60.03 | 50.03
370 |  |  |  | 0.03 | 60.03 | 50.03
371 |  |  |  | 0.03 | 60.03 | 50.03
372 |  |  |  | 0.03 | 60.03 | 50.03
373 |  |  |  | 0.03 | 60.03 | 50.03
374 |  |  |  | 0.03 | 60.03 | 50.03
375 |  |  |  | 0.03 | 60.03 | 50.03
376 |  |  |  | 0.03 | 60.03 | 50.03
377 |  |  |  | 0.03 | 60.03 | 50.03
378 |  |  |  | 0.03 | 60.03 | 50.03
379 |  |  |  | 0.03 | 60.03 | 50.03
380 |  |  |  | 0.03 | 60.03 | 50.03
381 |  |  |  | 0.03 | 60.03 | 50.03
382 |  |  |  | 0.03 | 60.03 | 50.03
383 |  |  |  | 0.03 | 60.03 | 50.03
384 |  |  |  | 0.03 | 60.03 | 50.03
385 |  |  |  | 0.03 | 60.03 | 50.03
386 |  |  |  | 0.03 | 60.03 | 50.03
387 |  |  |  | 0.03 | 60.03 | 50.03
388 |  |  |  | 0.03 | 60.03 | 50.03
389 |  |  |  | 0.03 | 60.03 | 50.03
390 |  |  |  | 0.03 | 60.03 | 50.03
391 |  |  |  | 0.03 | 60.03 | 50.03
392 |  |  |  | 0.03 | 60.03 | 50.03
393 |  |  |  | 0.03 | 60.03 | 50.03
394 |  |  |  | 0.03 | 60.03 | 50.03
395 |  |  |  | 0.03 | 60.03 | 50.03
396 |  |  |  | 0.03 | 60.03 | 50.03
397 |  |  |  | 0.03 | 60.03 | 50.03
398 |  |  |  | 0.03 | 60.03 | 50.03
399 |  |  |  | 0.03 | 60.03 | 50.03
400 |  |  |  | 0.03 | 60.03 | 50.03
401 |  |  |  | 0.03 | 60.03 | 50.03
402 |  |  |  | 0.03 | 60.03 | 50.03
403 |  |  |  | 0.03 | 60.03 | 50.03
404 |  |  |  | 0.03 | 60.03 | 50.03
405 |  |  |  | 0.03 | 60.03 | 50.03
406 |  |  |  | 0.03 | 60.03 | 50.03
407 |  |  |  | 0.03 | 60.03 | 50.03
408 |  |  |  | 0.03 | 60.03 | 50.03
409 |  |  |  | 0.03 | 60.03 | 50.03
410 |  |  |  | 0.03 | 60.03 | 50.03
411 |  |  |  | 0.03 | 60.03 | 50.03
412 |  |  |  | 0.03 | 60.03 | 50.03
413 |  |  |  | 0.03 | 60.03 | 50.03
414 |  |  |  | 0.03 | 60.03 | 50.03
415 |  |  |  | 0.03 | 60.03 | 50.03
416 |  |  |  | 0.03 | 60.03 | 50.03
417 |  |  |  | 0.03 | 60.03 | 50.03
418 |  |  |  | 0.03 | 60.03 | 50.03
419 |  |  |  | 0.03 | 60.03 | 50.03
420 |  |  |  | 0.03 | 60.03 | 50.03
421 |  |  |  | 0.03 | 60.03 | 50.03
422 |  |  |  | 0.03 | 60.03 | 50.03
423 |  |  |  | 0.03 | 60.03 | 50.03
424 |  |  |  | 0.03 | 60.03 | 50.03
425 |  |  |  | 0.03 | 60.03 | 50.03
426 |  |  |  | 0.03 | 60.03 | 50.03
427 |  |  |  | 0.03 | 60.03 | 50.03
428 |  |  |  | 0.03 | 60.03 | 50.03
429 |  |  |  | 0.03 | 60.03 | 50.03
430 |  |  |  | 0.03 | 60.03 | 50.03
431 |  |  |  | 0.03 | 60.03 | 50.03
432 |  |  |  | 0.03 | 60.03 | 50.03
433 |  |  |  | 0.03 | 60.03 | 50.03
434 |  |  |  | 0.03 | 60.03 | 50.03
435 |  |  |  | 0.03 | 60.03 | 50.03
436 |  |  |  | 0.03 | 60.03 | 50.03
437 |  |  |  | 0.03 | 60.03 | 50.03
438 |  |  |  | 0.03 | 60.03 | 50.03
439 |  |  |  | 0.03 | 60.03 | 50.03
440 |  |  |  | 0.03 | 60.03 | 50.03
441 |  |  |  | 0.03 | 60.03 | 50.03
442 |  |  |  | 0.03 | 60.03 | 50.03
443 |  |  |  | 0.03 | 60.03 | 50.03
444 |  |  |  | 0.03 | 60.03 | 50.03
445 |  |  |  | 0.03 | 60.03 | 50.03
446 |  |  |  | 0.03 | 60.03 | 50.03
447 |  |  |  | 0.03 | 60.03 | 50.03
448 |  |  |  | 0.03 | 60.03 | 50.03
449 |  |  |  | 0.03 | 60.03 | 50.03
450 |  |  |  | 0 | 60 | 50
451 |  |  |  | 0 | 60 | 50
452 |  |  |  | 0 | 60 | 50
453 |  |  |  | 0 | 60 | 50
454 |  |  |  | 0 | 60 | 50
455 |  |  |  | 0 | 60 | 50
456 |  |  |  | 0 | 60 | 50
457 |  |  |  | 0 | 60 | 50
458 |  |  |  | 0 | 60 | 50
459 |  |  |  | 0 | 60 | 50
460 |  |  |  | 0 | 60 | 50
461 |  |  |  | 0 | 60 | 50
462 |  |  |  | 0 | 60 | 50
463 |  |  |  | 0 | 60 | 50
464 |  |  |  | 0 | 60 | 50
465 |  |  |  | 0 | 60 | 50
466 |  |  |  | 0 | 60 | 50
467 |  |  |  | 0 | 60 | 50
468 |  |  |  | 0 | 60 | 50
469 |  |  |  | 0 | 60 | 50
470 |  |  |  | 0 | 60 | 50
471 |  |  |  | 0 | 60 | 50
472 |  |  |  | 0 | 60 | 50
473 |  |  |  | 0 | 60 | 50
474 |  |  |  | 0 | 60 | 50
475 |  |  |  | 0 | 60 | 50
476 |  |  |  | 0 | 60 | 50
477 |  |  |  | 0 | 60 | 50
478 |  |  |  | 0 | 60 | 50
479 |  |  |  | 0 | 60 | 50
480 |  |  |  | -0.03 | 59.97 | 49.97
481 |  |  |  | -0.03 | 59.97 | 49.97
482 |  |  |  | -0.03 | 59.97 | 49.97
483 |  |  |  | -0.03 | 59.97 | 49.97
484 |  |  |  | -0.03 | 59.97 | 49.97
485 |  |  |  | -0.03 | 59.97 | 49.97
486 |  |  |  | -0.03 | 59.97 | 49.97
487 |  |  |  | -0.03 | 59.97 | 49.97
488 |  |  |  | -0.03 | 59.97 | 49.97
489 |  |  |  | -0.03 | 59.97 | 49.97
490 |  |  |  | -0.03 | 59.97 | 49.97
491 |  |  |  | -0.03 | 59.97 | 49.97
492 |  |  |  | -0.03 | 59.97 | 49.97
493 |  |  |  | -0.03 | 59.97 | 49.97
494 |  |  |  | -0.03 | 59.97 | 49.97
495 |  |  |  | -0.03 | 59.97 | 49.97
496 |  |  |  | -0.03 | 59.97 | 49.97
497 |  |  |  | -0.03 | 59.97 | 49.97
498 |  |  |  | -0.03 | 59.97 | 49.97
499 |  |  |  | -0.03 | 59.97 | 49.97
500 |  |  |  | -0.03 | 59.97 | 49.97
501 |  |  |  | -0.03 | 59.97 | 49.97
502 |  |  |  | -0.03 | 59.97 | 49.97
503 |  |  |  | -0.03 | 59.97 | 49.97
504 |  |  |  | -0.03 | 59.97 | 49.97
505 |  |  |  | -0.03 | 59.97 | 49.97
506 |  |  |  | -0.03 | 59.97 | 49.97
507 |  |  |  | -0.03 | 59.97 | 49.97
508 |  |  |  | -0.03 | 59.97 | 49.97
509 |  |  |  | -0.03 | 59.97 | 49.97
510 |  |  |  | -0.03 | 59.97 | 49.97
511 |  |  |  | -0.03 | 59.97 | 49.97
512 |  |  |  | -0.03 | 59.97 | 49.97
513 |  |  |  | -0.03 | 59.97 | 49.97
514 |  |  |  | -0.03 | 59.97 | 49.97
515 |  |  |  | -0.03 | 59.97 | 49.97
516 |  |  |  | -0.03 | 59.97 | 49.97
517 |  |  |  | -0.03 | 59.97 | 49.97
518 |  |  |  | -0.03 | 59.97 | 49.97
519 |  |  |  | -0.03 | 59.97 | 49.97
520 |  |  |  | -0.03 | 59.97 | 49.97
521 |  |  |  | -0.03 | 59.97 | 49.97
522 |  |  |  | -0.03 | 59.97 | 49.97
523 |  |  |  | -0.03 | 59.97 | 49.97
524 |  |  |  | -0.03 | 59.97 | 49.97
525 |  |  |  | -0.03 | 59.97 | 49.97
526 |  |  |  | -0.03 | 59.97 | 49.97
527 |  |  |  | -0.03 | 59.97 | 49.97
528 |  |  |  | -0.03 | 59.97 | 49.97
529 |  |  |  | -0.03 | 59.97 | 49.97
530 |  |  |  | -0.03 | 59.97 | 49.97
531 |  |  |  | -0.03 | 59.97 | 49.97
532 |  |  |  | -0.03 | 59.97 | 49.97
533 |  |  |  | -0.03 | 59.97 | 49.97
534 |  |  |  | -0.03 | 59.97 | 49.97
535 |  |  |  | -0.03 | 59.97 | 49.97
536 |  |  |  | -0.03 | 59.97 | 49.97
537 |  |  |  | -0.03 | 59.97 | 49.97
538 |  |  |  | -0.03 | 59.97 | 49.97
539 |  |  |  | -0.03 | 59.97 | 49.97
540 |  |  |  | -0.03 | 59.97 | 49.97
541 |  |  |  | -0.03 | 59.97 | 49.97
542 |  |  |  | -0.03 | 59.97 | 49.97
543 |  |  |  | -0.03 | 59.97 | 49.97
544 |  |  |  | -0.03 | 59.97 | 49.97
545 |  |  |  | -0.03 | 59.97 | 49.97
546 |  |  |  | -0.03 | 59.97 | 49.97
547 |  |  |  | -0.03 | 59.97 | 49.97
548 |  |  |  | -0.03 | 59.97 | 49.97
549 |  |  |  | -0.03 | 59.97 | 49.97
550 |  |  |  | -0.03 | 59.97 | 49.97
551 |  |  |  | -0.03 | 59.97 | 49.97
552 |  |  |  | -0.03 | 59.97 | 49.97
553 |  |  |  | -0.03 | 59.97 | 49.97
554 |  |  |  | -0.03 | 59.97 | 49.97
555 |  |  |  | -0.03 | 59.97 | 49.97
556 |  |  |  | -0.03 | 59.97 | 49.97
557 |  |  |  | -0.03 | 59.97 | 49.97
558 |  |  |  | -0.03 | 59.97 | 49.97
559 |  |  |  | -0.03 | 59.97 | 49.97
560 |  |  |  | -0.03 | 59.97 | 49.97
561 |  |  |  | -0.03 | 59.97 | 49.97
562 |  |  |  | -0.03 | 59.97 | 49.97
563 |  |  |  | -0.03 | 59.97 | 49.97
564 |  |  |  | -0.03 | 59.97 | 49.97
565 |  |  |  | -0.03 | 59.97 | 49.97
566 |  |  |  | -0.03 | 59.97 | 49.97
567 |  |  |  | -0.03 | 59.97 | 49.97
568 |  |  |  | -0.03 | 59.97 | 49.97
569 |  |  |  | -0.03 | 59.97 | 49.97
570 |  |  |  | -0.03 | 59.97 | 49.97
571 |  |  |  | -0.03 | 59.97 | 49.97
572 |  |  |  | -0.03 | 59.97 | 49.97
573 |  |  |  | -0.03 | 59.97 | 49.97
574 |  |  |  | -0.03 | 59.97 | 49.97
575 |  |  |  | -0.03 | 59.97 | 49.97
576 |  |  |  | -0.03 | 59.97 | 49.97
577 |  |  |  | -0.03 | 59.97 | 49.97
578 |  |  |  | -0.03 | 59.97 | 49.97
579 |  |  |  | -0.03 | 59.97 | 49.97
580 |  |  |  | -0.03 | 59.97 | 49.97
581 |  |  |  | -0.03 | 59.97 | 49.97
582 |  |  |  | -0.03 | 59.97 | 49.97
583 |  |  |  | -0.03 | 59.97 | 49.97
584 |  |  |  | -0.03 | 59.97 | 49.97
585 |  |  |  | -0.03 | 59.97 | 49.97
586 |  |  |  | -0.03 | 59.97 | 49.97
587 |  |  |  | -0.03 | 59.97 | 49.97
588 |  |  |  | -0.03 | 59.97 | 49.97
589 |  |  |  | -0.03 | 59.97 | 49.97
590 |  |  |  | -0.03 | 59.97 | 49.97
591 |  |  |  | -0.03 | 59.97 | 49.97
592 |  |  |  | -0.03 | 59.97 | 49.97
593 |  |  |  | -0.03 | 59.97 | 49.97
594 |  |  |  | -0.03 | 59.97 | 49.97
595 |  |  |  | -0.03 | 59.97 | 49.97
596 |  |  |  | -0.03 | 59.97 | 49.97
597 |  |  |  | -0.03 | 59.97 | 49.97
598 |  |  |  | -0.03 | 59.97 | 49.97
599 |  |  |  | -0.03 | 59.97 | 49.97
600 |  |  |  | 0 | 60 | 50
601 |  |  |  | 0 | 60 | 50
602 |  |  |  | 0 | 60 | 50
603 |  |  |  | 0 | 60 | 50
604 |  |  |  | 0 | 60 | 50
605 |  |  |  | 0 | 60 | 50
606 |  |  |  | 0 | 60 | 50
607 |  |  |  | 0 | 60 | 50
608 |  |  |  | 0 | 60 | 50
609 |  |  |  | 0 | 60 | 50
610 |  |  |  | 0 | 60 | 50
611 |  |  |  | 0 | 60 | 50
612 |  |  |  | 0 | 60 | 50
613 |  |  |  | 0 | 60 | 50
614 |  |  |  | 0 | 60 | 50
615 |  |  |  | 0 | 60 | 50
616 |  |  |  | 0 | 60 | 50
617 |  |  |  | 0 | 60 | 50
618 |  |  |  | 0 | 60 | 50
619 |  |  |  | 0 | 60 | 50
620 |  |  |  | 0 | 60 | 50
621 |  |  |  | 0 | 60 | 50
622 |  |  |  | 0 | 60 | 50
623 |  |  |  | 0 | 60 | 50
624 |  |  |  | 0 | 60 | 50
625 |  |  |  | 0 | 60 | 50
626 |  |  |  | 0 | 60 | 50
627 |  |  |  | 0 | 60 | 50
628 |  |  |  | 0 | 60 | 50
629 |  |  |  | 0 | 60 | 50
630 |  |  |  | 0.05 | 60.05 | 50.05
631 |  |  |  | 0.05 | 60.05 | 50.05
632 |  |  |  | 0.05 | 60.05 | 50.05
633 |  |  |  | 0.05 | 60.05 | 50.05
634 |  |  |  | 0.05 | 60.05 | 50.05
635 |  |  |  | 0.05 | 60.05 | 50.05
636 |  |  |  | 0.05 | 60.05 | 50.05
637 |  |  |  | 0.05 | 60.05 | 50.05
638 |  |  |  | 0.05 | 60.05 | 50.05
639 |  |  |  | 0.05 | 60.05 | 50.05
640 |  |  |  | 0.05 | 60.05 | 50.05
641 |  |  |  | 0.05 | 60.05 | 50.05
642 |  |  |  | 0.05 | 60.05 | 50.05
643 |  |  |  | 0.05 | 60.05 | 50.05
644 |  |  |  | 0.05 | 60.05 | 50.05
645 |  |  |  | 0.05 | 60.05 | 50.05
646 |  |  |  | 0.05 | 60.05 | 50.05
647 |  |  |  | 0.05 | 60.05 | 50.05
648 |  |  |  | 0.05 | 60.05 | 50.05
649 |  |  |  | 0.05 | 60.05 | 50.05
650 |  |  |  | 0.05 | 60.05 | 50.05
651 |  |  |  | 0.05 | 60.05 | 50.05
652 |  |  |  | 0.05 | 60.05 | 50.05
653 |  |  |  | 0.05 | 60.05 | 50.05
654 |  |  |  | 0.05 | 60.05 | 50.05
655 |  |  |  | 0.05 | 60.05 | 50.05
656 |  |  |  | 0.05 | 60.05 | 50.05
657 |  |  |  | 0.05 | 60.05 | 50.05
658 |  |  |  | 0.05 | 60.05 | 50.05
659 |  |  |  | 0.05 | 60.05 | 50.05
660 |  |  |  | 0.05 | 60.05 | 50.05
661 |  |  |  | 0.05 | 60.05 | 50.05
662 |  |  |  | 0.05 | 60.05 | 50.05
663 |  |  |  | 0.05 | 60.05 | 50.05
664 |  |  |  | 0.05 | 60.05 | 50.05
665 |  |  |  | 0.05 | 60.05 | 50.05
666 |  |  |  | 0.05 | 60.05 | 50.05
667 |  |  |  | 0.05 | 60.05 | 50.05
668 |  |  |  | 0.05 | 60.05 | 50.05
669 |  |  |  | 0.05 | 60.05 | 50.05
670 |  |  |  | 0.05 | 60.05 | 50.05
671 |  |  |  | 0.05 | 60.05 | 50.05
672 |  |  |  | 0.05 | 60.05 | 50.05
673 |  |  |  | 0.05 | 60.05 | 50.05
674 |  |  |  | 0.05 | 60.05 | 50.05
675 |  |  |  | 0.05 | 60.05 | 50.05
676 |  |  |  | 0.05 | 60.05 | 50.05
677 |  |  |  | 0.05 | 60.05 | 50.05
678 |  |  |  | 0.05 | 60.05 | 50.05
679 |  |  |  | 0.05 | 60.05 | 50.05
680 |  |  |  | 0.05 | 60.05 | 50.05
681 |  |  |  | 0.05 | 60.05 | 50.05
682 |  |  |  | 0.05 | 60.05 | 50.05
683 |  |  |  | 0.05 | 60.05 | 50.05
684 |  |  |  | 0.05 | 60.05 | 50.05
685 |  |  |  | 0.05 | 60.05 | 50.05
686 |  |  |  | 0.05 | 60.05 | 50.05
687 |  |  |  | 0.05 | 60.05 | 50.05
688 |  |  |  | 0.05 | 60.05 | 50.05
689 |  |  |  | 0.05 | 60.05 | 50.05
690 |  |  |  | 0.05 | 60.05 | 50.05
691 |  |  |  | 0.05 | 60.05 | 50.05
692 |  |  |  | 0.05 | 60.05 | 50.05
693 |  |  |  | 0.05 | 60.05 | 50.05
694 |  |  |  | 0.05 | 60.05 | 50.05
695 |  |  |  | 0.05 | 60.05 | 50.05
696 |  |  |  | 0.05 | 60.05 | 50.05
697 |  |  |  | 0.05 | 60.05 | 50.05
698 |  |  |  | 0.05 | 60.05 | 50.05
699 |  |  |  | 0.05 | 60.05 | 50.05
700 |  |  |  | 0.05 | 60.05 | 50.05
701 |  |  |  | 0.05 | 60.05 | 50.05
702 |  |  |  | 0.05 | 60.05 | 50.05
703 |  |  |  | 0.05 | 60.05 | 50.05
704 |  |  |  | 0.05 | 60.05 | 50.05
705 |  |  |  | 0.05 | 60.05 | 50.05
706 |  |  |  | 0.05 | 60.05 | 50.05
707 |  |  |  | 0.05 | 60.05 | 50.05
708 |  |  |  | 0.05 | 60.05 | 50.05
709 |  |  |  | 0.05 | 60.05 | 50.05
710 |  |  |  | 0.05 | 60.05 | 50.05
711 |  |  |  | 0.05 | 60.05 | 50.05
712 |  |  |  | 0.05 | 60.05 | 50.05
713 |  |  |  | 0.05 | 60.05 | 50.05
714 |  |  |  | 0.05 | 60.05 | 50.05
715 |  |  |  | 0.05 | 60.05 | 50.05
716 |  |  |  | 0.05 | 60.05 | 50.05
717 |  |  |  | 0.05 | 60.05 | 50.05
718 |  |  |  | 0.05 | 60.05 | 50.05
719 |  |  |  | 0.05 | 60.05 | 50.05
720 |  |  |  | 0.05 | 60.05 | 50.05
721 |  |  |  | 0.05 | 60.05 | 50.05
722 |  |  |  | 0.05 | 60.05 | 50.05
723 |  |  |  | 0.05 | 60.05 | 50.05
724 |  |  |  | 0.05 | 60.05 | 50.05
725 |  |  |  | 0.05 | 60.05 | 50.05
726 |  |  |  | 0.05 | 60.05 | 50.05
727 |  |  |  | 0.05 | 60.05 | 50.05
728 |  |  |  | 0.05 | 60.05 | 50.05
729 |  |  |  | 0.05 | 60.05 | 50.05
730 |  |  |  | 0.05 | 60.05 | 50.05
731 |  |  |  | 0.05 | 60.05 | 50.05
732 |  |  |  | 0.05 | 60.05 | 50.05
733 |  |  |  | 0.05 | 60.05 | 50.05
734 |  |  |  | 0.05 | 60.05 | 50.05
735 |  |  |  | 0.05 | 60.05 | 50.05
736 |  |  |  | 0.05 | 60.05 | 50.05
737 |  |  |  | 0.05 | 60.05 | 50.05
738 |  |  |  | 0.05 | 60.05 | 50.05
739 |  |  |  | 0.05 | 60.05 | 50.05
740 |  |  |  | 0.05 | 60.05 | 50.05
741 |  |  |  | 0.05 | 60.05 | 50.05
742 |  |  |  | 0.05 | 60.05 | 50.05
743 |  |  |  | 0.05 | 60.05 | 50.05
744 |  |  |  | 0.05 | 60.05 | 50.05
745 |  |  |  | 0.05 | 60.05 | 50.05
746 |  |  |  | 0.05 | 60.05 | 50.05
747 |  |  |  | 0.05 | 60.05 | 50.05
748 |  |  |  | 0.05 | 60.05 | 50.05
749 |  |  |  | 0.05 | 60.05 | 50.05
750 |  |  |  | 0 | 60 | 50
751 |  |  |  | 0 | 60 | 50
752 |  |  |  | 0 | 60 | 50
753 |  |  |  | 0 | 60 | 50
754 |  |  |  | 0 | 60 | 50
755 |  |  |  | 0 | 60 | 50
756 |  |  |  | 0 | 60 | 50
757 |  |  |  | 0 | 60 | 50
758 |  |  |  | 0 | 60 | 50
759 |  |  |  | 0 | 60 | 50
760 |  |  |  | 0 | 60 | 50
761 |  |  |  | 0 | 60 | 50
762 |  |  |  | 0 | 60 | 50
763 |  |  |  | 0 | 60 | 50
764 |  |  |  | 0 | 60 | 50
765 |  |  |  | 0 | 60 | 50
766 |  |  |  | 0 | 60 | 50
767 |  |  |  | 0 | 60 | 50
768 |  |  |  | 0 | 60 | 50
769 |  |  |  | 0 | 60 | 50
770 |  |  |  | 0 | 60 | 50
771 |  |  |  | 0 | 60 | 50
772 |  |  |  | 0 | 60 | 50
773 |  |  |  | 0 | 60 | 50
774 |  |  |  | 0 | 60 | 50
775 |  |  |  | 0 | 60 | 50
776 |  |  |  | 0 | 60 | 50
777 |  |  |  | 0 | 60 | 50
778 |  |  |  | 0 | 60 | 50
779 |  |  |  | 0 | 60 | 50
780 |  |  |  | -0.05 | 59.95 | 49.95
781 |  |  |  | -0.05 | 59.95 | 49.95
782 |  |  |  | -0.05 | 59.95 | 49.95
783 |  |  |  | -0.05 | 59.95 | 49.95
784 |  |  |  | -0.05 | 59.95 | 49.95
785 |  |  |  | -0.05 | 59.95 | 49.95
786 |  |  |  | -0.05 | 59.95 | 49.95
787 |  |  |  | -0.05 | 59.95 | 49.95
788 |  |  |  | -0.05 | 59.95 | 49.95
789 |  |  |  | -0.05 | 59.95 | 49.95
790 |  |  |  | -0.05 | 59.95 | 49.95
791 |  |  |  | -0.05 | 59.95 | 49.95
792 |  |  |  | -0.05 | 59.95 | 49.95
793 |  |  |  | -0.05 | 59.95 | 49.95
794 |  |  |  | -0.05 | 59.95 | 49.95
795 |  |  |  | -0.05 | 59.95 | 49.95
796 |  |  |  | -0.05 | 59.95 | 49.95
797 |  |  |  | -0.05 | 59.95 | 49.95
798 |  |  |  | -0.05 | 59.95 | 49.95
799 |  |  |  | -0.05 | 59.95 | 49.95
800 |  |  |  | -0.05 | 59.95 | 49.95
801 |  |  |  | -0.05 | 59.95 | 49.95
802 |  |  |  | -0.05 | 59.95 | 49.95
803 |  |  |  | -0.05 | 59.95 | 49.95
804 |  |  |  | -0.05 | 59.95 | 49.95
805 |  |  |  | -0.05 | 59.95 | 49.95
806 |  |  |  | -0.05 | 59.95 | 49.95
807 |  |  |  | -0.05 | 59.95 | 49.95
808 |  |  |  | -0.05 | 59.95 | 49.95
809 |  |  |  | -0.05 | 59.95 | 49.95
810 |  |  |  | -0.05 | 59.95 | 49.95
811 |  |  |  | -0.05 | 59.95 | 49.95
812 |  |  |  | -0.05 | 59.95 | 49.95
813 |  |  |  | -0.05 | 59.95 | 49.95
814 |  |  |  | -0.05 | 59.95 | 49.95
815 |  |  |  | -0.05 | 59.95 | 49.95
816 |  |  |  | -0.05 | 59.95 | 49.95
817 |  |  |  | -0.05 | 59.95 | 49.95
818 |  |  |  | -0.05 | 59.95 | 49.95
819 |  |  |  | -0.05 | 59.95 | 49.95
820 |  |  |  | -0.05 | 59.95 | 49.95
821 |  |  |  | -0.05 | 59.95 | 49.95
822 |  |  |  | -0.05 | 59.95 | 49.95
823 |  |  |  | -0.05 | 59.95 | 49.95
824 |  |  |  | -0.05 | 59.95 | 49.95
825 |  |  |  | -0.05 | 59.95 | 49.95
826 |  |  |  | -0.05 | 59.95 | 49.95
827 |  |  |  | -0.05 | 59.95 | 49.95
828 |  |  |  | -0.05 | 59.95 | 49.95
829 |  |  |  | -0.05 | 59.95 | 49.95
830 |  |  |  | -0.05 | 59.95 | 49.95
831 |  |  |  | -0.05 | 59.95 | 49.95
832 |  |  |  | -0.05 | 59.95 | 49.95
833 |  |  |  | -0.05 | 59.95 | 49.95
834 |  |  |  | -0.05 | 59.95 | 49.95
835 |  |  |  | -0.05 | 59.95 | 49.95
836 |  |  |  | -0.05 | 59.95 | 49.95
837 |  |  |  | -0.05 | 59.95 | 49.95
838 |  |  |  | -0.05 | 59.95 | 49.95
839 |  |  |  | -0.05 | 59.95 | 49.95
840 |  |  |  | -0.05 | 59.95 | 49.95
841 |  |  |  | -0.05 | 59.95 | 49.95
842 |  |  |  | -0.05 | 59.95 | 49.95
843 |  |  |  | -0.05 | 59.95 | 49.95
844 |  |  |  | -0.05 | 59.95 | 49.95
845 |  |  |  | -0.05 | 59.95 | 49.95
846 |  |  |  | -0.05 | 59.95 | 49.95
847 |  |  |  | -0.05 | 59.95 | 49.95
848 |  |  |  | -0.05 | 59.95 | 49.95
849 |  |  |  | -0.05 | 59.95 | 49.95
850 |  |  |  | -0.05 | 59.95 | 49.95
851 |  |  |  | -0.05 | 59.95 | 49.95
852 |  |  |  | -0.05 | 59.95 | 49.95
853 |  |  |  | -0.05 | 59.95 | 49.95
854 |  |  |  | -0.05 | 59.95 | 49.95
855 |  |  |  | -0.05 | 59.95 | 49.95
856 |  |  |  | -0.05 | 59.95 | 49.95
857 |  |  |  | -0.05 | 59.95 | 49.95
858 |  |  |  | -0.05 | 59.95 | 49.95
859 |  |  |  | -0.05 | 59.95 | 49.95
860 |  |  |  | -0.05 | 59.95 | 49.95
861 |  |  |  | -0.05 | 59.95 | 49.95
862 |  |  |  | -0.05 | 59.95 | 49.95
863 |  |  |  | -0.05 | 59.95 | 49.95
864 |  |  |  | -0.05 | 59.95 | 49.95
865 |  |  |  | -0.05 | 59.95 | 49.95
866 |  |  |  | -0.05 | 59.95 | 49.95
867 |  |  |  | -0.05 | 59.95 | 49.95
868 |  |  |  | -0.05 | 59.95 | 49.95
869 |  |  |  | -0.05 | 59.95 | 49.95
870 |  |  |  | -0.05 | 59.95 | 49.95
871 |  |  |  | -0.05 | 59.95 | 49.95
872 |  |  |  | -0.05 | 59.95 | 49.95
873 |  |  |  | -0.05 | 59.95 | 49.95
874 |  |  |  | -0.05 | 59.95 | 49.95
875 |  |  |  | -0.05 | 59.95 | 49.95
876 |  |  |  | -0.05 | 59.95 | 49.95
877 |  |  |  | -0.05 | 59.95 | 49.95
878 |  |  |  | -0.05 | 59.95 | 49.95
879 |  |  |  | -0.05 | 59.95 | 49.95
880 |  |  |  | -0.05 | 59.95 | 49.95
881 |  |  |  | -0.05 | 59.95 | 49.95
882 |  |  |  | -0.05 | 59.95 | 49.95
883 |  |  |  | -0.05 | 59.95 | 49.95
884 |  |  |  | -0.05 | 59.95 | 49.95
885 |  |  |  | -0.05 | 59.95 | 49.95
886 |  |  |  | -0.05 | 59.95 | 49.95
887 |  |  |  | -0.05 | 59.95 | 49.95
888 |  |  |  | -0.05 | 59.95 | 49.95
889 |  |  |  | -0.05 | 59.95 | 49.95
890 |  |  |  | -0.05 | 59.95 | 49.95
891 |  |  |  | -0.05 | 59.95 | 49.95
892 |  |  |  | -0.05 | 59.95 | 49.95
893 |  |  |  | -0.05 | 59.95 | 49.95
894 |  |  |  | -0.05 | 59.95 | 49.95
895 |  |  |  | -0.05 | 59.95 | 49.95
896 |  |  |  | -0.05 | 59.95 | 49.95
897 |  |  |  | -0.05 | 59.95 | 49.95
898 |  |  |  | -0.05 | 59.95 | 49.95
899 |  |  |  | -0.05 | 59.95 | 49.95
900 |  |  |  | 0 | 60 | 50
901 |  |  |  | 0 | 60 | 50
902 |  |  |  | 0 | 60 | 50
903 |  |  |  | 0 | 60 | 50
904 |  |  |  | 0 | 60 | 50
905 |  |  |  | 0 | 60 | 50
906 |  |  |  | 0 | 60 | 50
907 |  |  |  | 0 | 60 | 50
908 |  |  |  | 0 | 60 | 50
909 |  |  |  | 0 | 60 | 50
910 |  |  |  | 0 | 60 | 50
911 |  |  |  | 0 | 60 | 50
912 |  |  |  | 0 | 60 | 50
913 |  |  |  | 0 | 60 | 50
914 |  |  |  | 0 | 60 | 50
915 |  |  |  | 0 | 60 | 50
916 |  |  |  | 0 | 60 | 50
917 |  |  |  | 0 | 60 | 50
918 |  |  |  | 0 | 60 | 50
919 |  |  |  | 0 | 60 | 50
920 |  |  |  | 0 | 60 | 50
921 |  |  |  | 0 | 60 | 50
922 |  |  |  | 0 | 60 | 50
923 |  |  |  | 0 | 60 | 50
924 |  |  |  | 0 | 60 | 50
925 |  |  |  | 0 | 60 | 50
926 |  |  |  | 0 | 60 | 50
927 |  |  |  | 0 | 60 | 50
928 |  |  |  | 0 | 60 | 50
929 |  |  |  | 0 | 60 | 50
930 |  |  |  | 0.08 | 60.08 | 50.08
931 |  |  |  | 0.08 | 60.08 | 50.08
932 |  |  |  | 0.08 | 60.08 | 50.08
933 |  |  |  | 0.08 | 60.08 | 50.08
934 |  |  |  | 0.08 | 60.08 | 50.08
935 |  |  |  | 0.08 | 60.08 | 50.08
936 |  |  |  | 0.08 | 60.08 | 50.08
937 |  |  |  | 0.08 | 60.08 | 50.08
938 |  |  |  | 0.08 | 60.08 | 50.08
939 |  |  |  | 0.08 | 60.08 | 50.08
940 |  |  |  | 0.08 | 60.08 | 50.08
941 |  |  |  | 0.08 | 60.08 | 50.08
942 |  |  |  | 0.08 | 60.08 | 50.08
943 |  |  |  | 0.08 | 60.08 | 50.08
944 |  |  |  | 0.08 | 60.08 | 50.08
945 |  |  |  | 0.08 | 60.08 | 50.08
946 |  |  |  | 0.08 | 60.08 | 50.08
947 |  |  |  | 0.08 | 60.08 | 50.08
948 |  |  |  | 0.08 | 60.08 | 50.08
949 |  |  |  | 0.08 | 60.08 | 50.08
950 |  |  |  | 0.08 | 60.08 | 50.08
951 |  |  |  | 0.08 | 60.08 | 50.08
952 |  |  |  | 0.08 | 60.08 | 50.08
953 |  |  |  | 0.08 | 60.08 | 50.08
954 |  |  |  | 0.08 | 60.08 | 50.08
955 |  |  |  | 0.08 | 60.08 | 50.08
956 |  |  |  | 0.08 | 60.08 | 50.08
957 |  |  |  | 0.08 | 60.08 | 50.08
958 |  |  |  | 0.08 | 60.08 | 50.08
959 |  |  |  | 0.08 | 60.08 | 50.08
960 |  |  |  | 0.08 | 60.08 | 50.08
961 |  |  |  | 0.08 | 60.08 | 50.08
962 |  |  |  | 0.08 | 60.08 | 50.08
963 |  |  |  | 0.08 | 60.08 | 50.08
964 |  |  |  | 0.08 | 60.08 | 50.08
965 |  |  |  | 0.08 | 60.08 | 50.08
966 |  |  |  | 0.08 | 60.08 | 50.08
967 |  |  |  | 0.08 | 60.08 | 50.08
968 |  |  |  | 0.08 | 60.08 | 50.08
969 |  |  |  | 0.08 | 60.08 | 50.08
970 |  |  |  | 0.08 | 60.08 | 50.08
971 |  |  |  | 0.08 | 60.08 | 50.08
972 |  |  |  | 0.08 | 60.08 | 50.08
973 |  |  |  | 0.08 | 60.08 | 50.08
974 |  |  |  | 0.08 | 60.08 | 50.08
975 |  |  |  | 0.08 | 60.08 | 50.08
976 |  |  |  | 0.08 | 60.08 | 50.08
977 |  |  |  | 0.08 | 60.08 | 50.08
978 |  |  |  | 0.08 | 60.08 | 50.08
979 |  |  |  | 0.08 | 60.08 | 50.08
980 |  |  |  | 0.08 | 60.08 | 50.08
981 |  |  |  | 0.08 | 60.08 | 50.08
982 |  |  |  | 0.08 | 60.08 | 50.08
983 |  |  |  | 0.08 | 60.08 | 50.08
984 |  |  |  | 0.08 | 60.08 | 50.08
985 |  |  |  | 0.08 | 60.08 | 50.08
986 |  |  |  | 0.08 | 60.08 | 50.08
987 |  |  |  | 0.08 | 60.08 | 50.08
988 |  |  |  | 0.08 | 60.08 | 50.08
989 |  |  |  | 0.08 | 60.08 | 50.08
990 |  |  |  | 0.08 | 60.08 | 50.08
991 |  |  |  | 0.08 | 60.08 | 50.08
992 |  |  |  | 0.08 | 60.08 | 50.08
993 |  |  |  | 0.08 | 60.08 | 50.08
994 |  |  |  | 0.08 | 60.08 | 50.08
995 |  |  |  | 0.08 | 60.08 | 50.08
996 |  |  |  | 0.08 | 60.08 | 50.08
997 |  |  |  | 0.08 | 60.08 | 50.08
998 |  |  |  | 0.08 | 60.08 | 50.08
999 |  |  |  | 0.08 | 60.08 | 50.08
1000 |  |  |  | 0.08 | 60.08 | 50.08
1001 |  |  |  | 0.08 | 60.08 | 50.08
1002 |  |  |  | 0.08 | 60.08 | 50.08
1003 |  |  |  | 0.08 | 60.08 | 50.08
1004 |  |  |  | 0.08 | 60.08 | 50.08
1005 |  |  |  | 0.08 | 60.08 | 50.08
1006 |  |  |  | 0.08 | 60.08 | 50.08
1007 |  |  |  | 0.08 | 60.08 | 50.08
1008 |  |  |  | 0.08 | 60.08 | 50.08
1009 |  |  |  | 0.08 | 60.08 | 50.08
1010 |  |  |  | 0.08 | 60.08 | 50.08
1011 |  |  |  | 0.08 | 60.08 | 50.08
1012 |  |  |  | 0.08 | 60.08 | 50.08
1013 |  |  |  | 0.08 | 60.08 | 50.08
1014 |  |  |  | 0.08 | 60.08 | 50.08
1015 |  |  |  | 0.08 | 60.08 | 50.08
1016 |  |  |  | 0.08 | 60.08 | 50.08
1017 |  |  |  | 0.08 | 60.08 | 50.08
1018 |  |  |  | 0.08 | 60.08 | 50.08
1019 |  |  |  | 0.08 | 60.08 | 50.08
1020 |  |  |  | 0.08 | 60.08 | 50.08
1021 |  |  |  | 0.08 | 60.08 | 50.08
1022 |  |  |  | 0.08 | 60.08 | 50.08
1023 |  |  |  | 0.08 | 60.08 | 50.08
1024 |  |  |  | 0.08 | 60.08 | 50.08
1025 |  |  |  | 0.08 | 60.08 | 50.08
1026 |  |  |  | 0.08 | 60.08 | 50.08
1027 |  |  |  | 0.08 | 60.08 | 50.08
1028 |  |  |  | 0.08 | 60.08 | 50.08
1029 |  |  |  | 0.08 | 60.08 | 50.08
1030 |  |  |  | 0.08 | 60.08 | 50.08
1031 |  |  |  | 0.08 | 60.08 | 50.08
1032 |  |  |  | 0.08 | 60.08 | 50.08
1033 |  |  |  | 0.08 | 60.08 | 50.08
1034 |  |  |  | 0.08 | 60.08 | 50.08
1035 |  |  |  | 0.08 | 60.08 | 50.08
1036 |  |  |  | 0.08 | 60.08 | 50.08
1037 |  |  |  | 0.08 | 60.08 | 50.08
1038 |  |  |  | 0.08 | 60.08 | 50.08
1039 |  |  |  | 0.08 | 60.08 | 50.08
1040 |  |  |  | 0.08 | 60.08 | 50.08
1041 |  |  |  | 0.08 | 60.08 | 50.08
1042 |  |  |  | 0.08 | 60.08 | 50.08
1043 |  |  |  | 0.08 | 60.08 | 50.08
1044 |  |  |  | 0.08 | 60.08 | 50.08
1045 |  |  |  | 0.08 | 60.08 | 50.08
1046 |  |  |  | 0.08 | 60.08 | 50.08
1047 |  |  |  | 0.08 | 60.08 | 50.08
1048 |  |  |  | 0.08 | 60.08 | 50.08
1049 |  |  |  | 0.08 | 60.08 | 50.08
1050 |  |  |  | 0 | 60 | 50
1051 |  |  |  | 0 | 60 | 50
1052 |  |  |  | 0 | 60 | 50
1053 |  |  |  | 0 | 60 | 50
1054 |  |  |  | 0 | 60 | 50
1055 |  |  |  | 0 | 60 | 50
1056 |  |  |  | 0 | 60 | 50
1057 |  |  |  | 0 | 60 | 50
1058 |  |  |  | 0 | 60 | 50
1059 |  |  |  | 0 | 60 | 50
1060 |  |  |  | 0 | 60 | 50
1061 |  |  |  | 0 | 60 | 50
1062 |  |  |  | 0 | 60 | 50
1063 |  |  |  | 0 | 60 | 50
1064 |  |  |  | 0 | 60 | 50
1065 |  |  |  | 0 | 60 | 50
1066 |  |  |  | 0 | 60 | 50
1067 |  |  |  | 0 | 60 | 50
1068 |  |  |  | 0 | 60 | 50
1069 |  |  |  | 0 | 60 | 50
1070 |  |  |  | 0 | 60 | 50
1071 |  |  |  | 0 | 60 | 50
1072 |  |  |  | 0 | 60 | 50
1073 |  |  |  | 0 | 60 | 50
1074 |  |  |  | 0 | 60 | 50
1075 |  |  |  | 0 | 60 | 50
1076 |  |  |  | 0 | 60 | 50
1077 |  |  |  | 0 | 60 | 50
1078 |  |  |  | 0 | 60 | 50
1079 |  |  |  | 0 | 60 | 50
1080 |  |  |  | -0.08 | 59.92 | 49.92
1081 |  |  |  | -0.08 | 59.92 | 49.92
1082 |  |  |  | -0.08 | 59.92 | 49.92
1083 |  |  |  | -0.08 | 59.92 | 49.92
1084 |  |  |  | -0.08 | 59.92 | 49.92
1085 |  |  |  | -0.08 | 59.92 | 49.92
1086 |  |  |  | -0.08 | 59.92 | 49.92
1087 |  |  |  | -0.08 | 59.92 | 49.92
1088 |  |  |  | -0.08 | 59.92 | 49.92
1089 |  |  |  | -0.08 | 59.92 | 49.92
1090 |  |  |  | -0.08 | 59.92 | 49.92
1091 |  |  |  | -0.08 | 59.92 | 49.92
1092 |  |  |  | -0.08 | 59.92 | 49.92
1093 |  |  |  | -0.08 | 59.92 | 49.92
1094 |  |  |  | -0.08 | 59.92 | 49.92
1095 |  |  |  | -0.08 | 59.92 | 49.92
1096 |  |  |  | -0.08 | 59.92 | 49.92
1097 |  |  |  | -0.08 | 59.92 | 49.92
1098 |  |  |  | -0.08 | 59.92 | 49.92
1099 |  |  |  | -0.08 | 59.92 | 49.92
1100 |  |  |  | -0.08 | 59.92 | 49.92
1101 |  |  |  | -0.08 | 59.92 | 49.92
1102 |  |  |  | -0.08 | 59.92 | 49.92
1103 |  |  |  | -0.08 | 59.92 | 49.92
1104 |  |  |  | -0.08 | 59.92 | 49.92
1105 |  |  |  | -0.08 | 59.92 | 49.92
1106 |  |  |  | -0.08 | 59.92 | 49.92
1107 |  |  |  | -0.08 | 59.92 | 49.92
1108 |  |  |  | -0.08 | 59.92 | 49.92
1109 |  |  |  | -0.08 | 59.92 | 49.92
1110 |  |  |  | -0.08 | 59.92 | 49.92
1111 |  |  |  | -0.08 | 59.92 | 49.92
1112 |  |  |  | -0.08 | 59.92 | 49.92
1113 |  |  |  | -0.08 | 59.92 | 49.92
1114 |  |  |  | -0.08 | 59.92 | 49.92
1115 |  |  |  | -0.08 | 59.92 | 49.92
1116 |  |  |  | -0.08 | 59.92 | 49.92
1117 |  |  |  | -0.08 | 59.92 | 49.92
1118 |  |  |  | -0.08 | 59.92 | 49.92
1119 |  |  |  | -0.08 | 59.92 | 49.92
1120 |  |  |  | -0.08 | 59.92 | 49.92
1121 |  |  |  | -0.08 | 59.92 | 49.92
1122 |  |  |  | -0.08 | 59.92 | 49.92
1123 |  |  |  | -0.08 | 59.92 | 49.92
1124 |  |  |  | -0.08 | 59.92 | 49.92
1125 |  |  |  | -0.08 | 59.92 | 49.92
1126 |  |  |  | -0.08 | 59.92 | 49.92
1127 |  |  |  | -0.08 | 59.92 | 49.92
1128 |  |  |  | -0.08 | 59.92 | 49.92
1129 |  |  |  | -0.08 | 59.92 | 49.92
1130 |  |  |  | -0.08 | 59.92 | 49.92
1131 |  |  |  | -0.08 | 59.92 | 49.92
1132 |  |  |  | -0.08 | 59.92 | 49.92
1133 |  |  |  | -0.08 | 59.92 | 49.92
1134 |  |  |  | -0.08 | 59.92 | 49.92
1135 |  |  |  | -0.08 | 59.92 | 49.92
1136 |  |  |  | -0.08 | 59.92 | 49.92
1137 |  |  |  | -0.08 | 59.92 | 49.92
1138 |  |  |  | -0.08 | 59.92 | 49.92
1139 |  |  |  | -0.08 | 59.92 | 49.92
1140 |  |  |  | -0.08 | 59.92 | 49.92
1141 |  |  |  | -0.08 | 59.92 | 49.92
1142 |  |  |  | -0.08 | 59.92 | 49.92
1143 |  |  |  | -0.08 | 59.92 | 49.92
1144 |  |  |  | -0.08 | 59.92 | 49.92
1145 |  |  |  | -0.08 | 59.92 | 49.92
1146 |  |  |  | -0.08 | 59.92 | 49.92
1147 |  |  |  | -0.08 | 59.92 | 49.92
1148 |  |  |  | -0.08 | 59.92 | 49.92
1149 |  |  |  | -0.08 | 59.92 | 49.92
1150 |  |  |  | -0.08 | 59.92 | 49.92
1151 |  |  |  | -0.08 | 59.92 | 49.92
1152 |  |  |  | -0.08 | 59.92 | 49.92
1153 |  |  |  | -0.08 | 59.92 | 49.92
1154 |  |  |  | -0.08 | 59.92 | 49.92
1155 |  |  |  | -0.08 | 59.92 | 49.92
1156 |  |  |  | -0.08 | 59.92 | 49.92
1157 |  |  |  | -0.08 | 59.92 | 49.92
1158 |  |  |  | -0.08 | 59.92 | 49.92
1159 |  |  |  | -0.08 | 59.92 | 49.92
1160 |  |  |  | -0.08 | 59.92 | 49.92
1161 |  |  |  | -0.08 | 59.92 | 49.92
1162 |  |  |  | -0.08 | 59.92 | 49.92
1163 |  |  |  | -0.08 | 59.92 | 49.92
1164 |  |  |  | -0.08 | 59.92 | 49.92
1165 |  |  |  | -0.08 | 59.92 | 49.92
1166 |  |  |  | -0.08 | 59.92 | 49.92
1167 |  |  |  | -0.08 | 59.92 | 49.92
1168 |  |  |  | -0.08 | 59.92 | 49.92
1169 |  |  |  | -0.08 | 59.92 | 49.92
1170 |  |  |  | -0.08 | 59.92 | 49.92
1171 |  |  |  | -0.08 | 59.92 | 49.92
1172 |  |  |  | -0.08 | 59.92 | 49.92
1173 |  |  |  | -0.08 | 59.92 | 49.92
1174 |  |  |  | -0.08 | 59.92 | 49.92
1175 |  |  |  | -0.08 | 59.92 | 49.92
1176 |  |  |  | -0.08 | 59.92 | 49.92
1177 |  |  |  | -0.08 | 59.92 | 49.92
1178 |  |  |  | -0.08 | 59.92 | 49.92
1179 |  |  |  | -0.08 | 59.92 | 49.92
1180 |  |  |  | -0.08 | 59.92 | 49.92
1181 |  |  |  | -0.08 | 59.92 | 49.92
1182 |  |  |  | -0.08 | 59.92 | 49.92
1183 |  |  |  | -0.08 | 59.92 | 49.92
1184 |  |  |  | -0.08 | 59.92 | 49.92
1185 |  |  |  | -0.08 | 59.92 | 49.92
1186 |  |  |  | -0.08 | 59.92 | 49.92
1187 |  |  |  | -0.08 | 59.92 | 49.92
1188 |  |  |  | -0.08 | 59.92 | 49.92
1189 |  |  |  | -0.08 | 59.92 | 49.92
1190 |  |  |  | -0.08 | 59.92 | 49.92
1191 |  |  |  | -0.08 | 59.92 | 49.92
1192 |  |  |  | -0.08 | 59.92 | 49.92
1193 |  |  |  | -0.08 | 59.92 | 49.92
1194 |  |  |  | -0.08 | 59.92 | 49.92
1195 |  |  |  | -0.08 | 59.92 | 49.92
1196 |  |  |  | -0.08 | 59.92 | 49.92
1197 |  |  |  | -0.08 | 59.92 | 49.92
1198 |  |  |  | -0.08 | 59.92 | 49.92
1199 |  |  |  | -0.08 | 59.92 | 49.92
1200 |  |  |  | 0 | 60 | 50
1201 |  |  |  | 0 | 60 | 50
1202 |  |  |  | 0 | 60 | 50
1203 |  |  |  | 0 | 60 | 50
1204 |  |  |  | 0 | 60 | 50
1205 |  |  |  | 0 | 60 | 50
1206 |  |  |  | 0 | 60 | 50
1207 |  |  |  | 0 | 60 | 50
1208 |  |  |  | 0 | 60 | 50
1209 |  |  |  | 0 | 60 | 50
1210 |  |  |  | 0 | 60 | 50
1211 |  |  |  | 0 | 60 | 50
1212 |  |  |  | 0 | 60 | 50
1213 |  |  |  | 0 | 60 | 50
1214 |  |  |  | 0 | 60 | 50
1215 |  |  |  | 0 | 60 | 50
1216 |  |  |  | 0 | 60 | 50
1217 |  |  |  | 0 | 60 | 50
1218 |  |  |  | 0 | 60 | 50
1219 |  |  |  | 0 | 60 | 50
1220 |  |  |  | 0 | 60 | 50
1221 |  |  |  | 0 | 60 | 50
1222 |  |  |  | 0 | 60 | 50
1223 |  |  |  | 0 | 60 | 50
1224 |  |  |  | 0 | 60 | 50
1225 |  |  |  | 0 | 60 | 50
1226 |  |  |  | 0 | 60 | 50
1227 |  |  |  | 0 | 60 | 50
1228 |  |  |  | 0 | 60 | 50
1229 |  |  |  | 0 | 60 | 50
1230 |  |  |  | 0.12 | 60.12 | 50.12
1231 |  |  |  | 0.12 | 60.12 | 50.12
1232 |  |  |  | 0.12 | 60.12 | 50.12
1233 |  |  |  | 0.12 | 60.12 | 50.12
1234 |  |  |  | 0.12 | 60.12 | 50.12
1235 |  |  |  | 0.12 | 60.12 | 50.12
1236 |  |  |  | 0.12 | 60.12 | 50.12
1237 |  |  |  | 0.12 | 60.12 | 50.12
1238 |  |  |  | 0.12 | 60.12 | 50.12
1239 |  |  |  | 0.12 | 60.12 | 50.12
1240 |  |  |  | 0.12 | 60.12 | 50.12
1241 |  |  |  | 0.12 | 60.12 | 50.12
1242 |  |  |  | 0.12 | 60.12 | 50.12
1243 |  |  |  | 0.12 | 60.12 | 50.12
1244 |  |  |  | 0.12 | 60.12 | 50.12
1245 |  |  |  | 0.12 | 60.12 | 50.12
1246 |  |  |  | 0.12 | 60.12 | 50.12
1247 |  |  |  | 0.12 | 60.12 | 50.12
1248 |  |  |  | 0.12 | 60.12 | 50.12
1249 |  |  |  | 0.12 | 60.12 | 50.12
1250 |  |  |  | 0.12 | 60.12 | 50.12
1251 |  |  |  | 0.12 | 60.12 | 50.12
1252 |  |  |  | 0.12 | 60.12 | 50.12
1253 |  |  |  | 0.12 | 60.12 | 50.12
1254 |  |  |  | 0.12 | 60.12 | 50.12
1255 |  |  |  | 0.12 | 60.12 | 50.12
1256 |  |  |  | 0.12 | 60.12 | 50.12
1257 |  |  |  | 0.12 | 60.12 | 50.12
1258 |  |  |  | 0.12 | 60.12 | 50.12
1259 |  |  |  | 0.12 | 60.12 | 50.12
1260 |  |  |  | 0.12 | 60.12 | 50.12
1261 |  |  |  | 0.12 | 60.12 | 50.12
1262 |  |  |  | 0.12 | 60.12 | 50.12
1263 |  |  |  | 0.12 | 60.12 | 50.12
1264 |  |  |  | 0.12 | 60.12 | 50.12
1265 |  |  |  | 0.12 | 60.12 | 50.12
1266 |  |  |  | 0.12 | 60.12 | 50.12
1267 |  |  |  | 0.12 | 60.12 | 50.12
1268 |  |  |  | 0.12 | 60.12 | 50.12
1269 |  |  |  | 0.12 | 60.12 | 50.12
1270 |  |  |  | 0.12 | 60.12 | 50.12
1271 |  |  |  | 0.12 | 60.12 | 50.12
1272 |  |  |  | 0.12 | 60.12 | 50.12
1273 |  |  |  | 0.12 | 60.12 | 50.12
1274 |  |  |  | 0.12 | 60.12 | 50.12
1275 |  |  |  | 0.12 | 60.12 | 50.12
1276 |  |  |  | 0.12 | 60.12 | 50.12
1277 |  |  |  | 0.12 | 60.12 | 50.12
1278 |  |  |  | 0.12 | 60.12 | 50.12
1279 |  |  |  | 0.12 | 60.12 | 50.12
1280 |  |  |  | 0.12 | 60.12 | 50.12
1281 |  |  |  | 0.12 | 60.12 | 50.12
1282 |  |  |  | 0.12 | 60.12 | 50.12
1283 |  |  |  | 0.12 | 60.12 | 50.12
1284 |  |  |  | 0.12 | 60.12 | 50.12
1285 |  |  |  | 0.12 | 60.12 | 50.12
1286 |  |  |  | 0.12 | 60.12 | 50.12
1287 |  |  |  | 0.12 | 60.12 | 50.12
1288 |  |  |  | 0.12 | 60.12 | 50.12
1289 |  |  |  | 0.12 | 60.12 | 50.12
1290 |  |  |  | 0.12 | 60.12 | 50.12
1291 |  |  |  | 0.12 | 60.12 | 50.12
1292 |  |  |  | 0.12 | 60.12 | 50.12
1293 |  |  |  | 0.12 | 60.12 | 50.12
1294 |  |  |  | 0.12 | 60.12 | 50.12
1295 |  |  |  | 0.12 | 60.12 | 50.12
1296 |  |  |  | 0.12 | 60.12 | 50.12
1297 |  |  |  | 0.12 | 60.12 | 50.12
1298 |  |  |  | 0.12 | 60.12 | 50.12
1299 |  |  |  | 0.12 | 60.12 | 50.12
1300 |  |  |  | 0.12 | 60.12 | 50.12
1301 |  |  |  | 0.12 | 60.12 | 50.12
1302 |  |  |  | 0.12 | 60.12 | 50.12
1303 |  |  |  | 0.12 | 60.12 | 50.12
1304 |  |  |  | 0.12 | 60.12 | 50.12
1305 |  |  |  | 0.12 | 60.12 | 50.12
1306 |  |  |  | 0.12 | 60.12 | 50.12
1307 |  |  |  | 0.12 | 60.12 | 50.12
1308 |  |  |  | 0.12 | 60.12 | 50.12
1309 |  |  |  | 0.12 | 60.12 | 50.12
1310 |  |  |  | 0.12 | 60.12 | 50.12
1311 |  |  |  | 0.12 | 60.12 | 50.12
1312 |  |  |  | 0.12 | 60.12 | 50.12
1313 |  |  |  | 0.12 | 60.12 | 50.12
1314 |  |  |  | 0.12 | 60.12 | 50.12
1315 |  |  |  | 0.12 | 60.12 | 50.12
1316 |  |  |  | 0.12 | 60.12 | 50.12
1317 |  |  |  | 0.12 | 60.12 | 50.12
1318 |  |  |  | 0.12 | 60.12 | 50.12
1319 |  |  |  | 0.12 | 60.12 | 50.12
1320 |  |  |  | 0.12 | 60.12 | 50.12
1321 |  |  |  | 0.12 | 60.12 | 50.12
1322 |  |  |  | 0.12 | 60.12 | 50.12
1323 |  |  |  | 0.12 | 60.12 | 50.12
1324 |  |  |  | 0.12 | 60.12 | 50.12
1325 |  |  |  | 0.12 | 60.12 | 50.12
1326 |  |  |  | 0.12 | 60.12 | 50.12
1327 |  |  |  | 0.12 | 60.12 | 50.12
1328 |  |  |  | 0.12 | 60.12 | 50.12
1329 |  |  |  | 0.12 | 60.12 | 50.12
1330 |  |  |  | 0.12 | 60.12 | 50.12
1331 |  |  |  | 0.12 | 60.12 | 50.12
1332 |  |  |  | 0.12 | 60.12 | 50.12
1333 |  |  |  | 0.12 | 60.12 | 50.12
1334 |  |  |  | 0.12 | 60.12 | 50.12
1335 |  |  |  | 0.12 | 60.12 | 50.12
1336 |  |  |  | 0.12 | 60.12 | 50.12
1337 |  |  |  | 0.12 | 60.12 | 50.12
1338 |  |  |  | 0.12 | 60.12 | 50.12
1339 |  |  |  | 0.12 | 60.12 | 50.12
1340 |  |  |  | 0.12 | 60.12 | 50.12
1341 |  |  |  | 0.12 | 60.12 | 50.12
1342 |  |  |  | 0.12 | 60.12 | 50.12
1343 |  |  |  | 0.12 | 60.12 | 50.12
1344 |  |  |  | 0.12 | 60.12 | 50.12
1345 |  |  |  | 0.12 | 60.12 | 50.12
1346 |  |  |  | 0.12 | 60.12 | 50.12
1347 |  |  |  | 0.12 | 60.12 | 50.12
1348 |  |  |  | 0.12 | 60.12 | 50.12
1349 |  |  |  | 0.12 | 60.12 | 50.12
1350 |  |  |  | 0 | 60 | 50
1351 |  |  |  | 0 | 60 | 50
1352 |  |  |  | 0 | 60 | 50
1353 |  |  |  | 0 | 60 | 50
1354 |  |  |  | 0 | 60 | 50
1355 |  |  |  | 0 | 60 | 50
1356 |  |  |  | 0 | 60 | 50
1357 |  |  |  | 0 | 60 | 50
1358 |  |  |  | 0 | 60 | 50
1359 |  |  |  | 0 | 60 | 50
1360 |  |  |  | 0 | 60 | 50
1361 |  |  |  | 0 | 60 | 50
1362 |  |  |  | 0 | 60 | 50
1363 |  |  |  | 0 | 60 | 50
1364 |  |  |  | 0 | 60 | 50
1365 |  |  |  | 0 | 60 | 50
1366 |  |  |  | 0 | 60 | 50
1367 |  |  |  | 0 | 60 | 50
1368 |  |  |  | 0 | 60 | 50
1369 |  |  |  | 0 | 60 | 50
1370 |  |  |  | 0 | 60 | 50
1371 |  |  |  | 0 | 60 | 50
1372 |  |  |  | 0 | 60 | 50
1373 |  |  |  | 0 | 60 | 50
1374 |  |  |  | 0 | 60 | 50
1375 |  |  |  | 0 | 60 | 50
1376 |  |  |  | 0 | 60 | 50
1377 |  |  |  | 0 | 60 | 50
1378 |  |  |  | 0 | 60 | 50
1379 |  |  |  | 0 | 60 | 50
1380 |  |  |  | -0.12 | 59.88 | 49.88
1381 |  |  |  | -0.12 | 59.88 | 49.88
1382 |  |  |  | -0.12 | 59.88 | 49.88
1383 |  |  |  | -0.12 | 59.88 | 49.88
1384 |  |  |  | -0.12 | 59.88 | 49.88
1385 |  |  |  | -0.12 | 59.88 | 49.88
1386 |  |  |  | -0.12 | 59.88 | 49.88
1387 |  |  |  | -0.12 | 59.88 | 49.88
1388 |  |  |  | -0.12 | 59.88 | 49.88
1389 |  |  |  | -0.12 | 59.88 | 49.88
1390 |  |  |  | -0.12 | 59.88 | 49.88
1391 |  |  |  | -0.12 | 59.88 | 49.88
1392 |  |  |  | -0.12 | 59.88 | 49.88
1393 |  |  |  | -0.12 | 59.88 | 49.88
1394 |  |  |  | -0.12 | 59.88 | 49.88
1395 |  |  |  | -0.12 | 59.88 | 49.88
1396 |  |  |  | -0.12 | 59.88 | 49.88
1397 |  |  |  | -0.12 | 59.88 | 49.88
1398 |  |  |  | -0.12 | 59.88 | 49.88
1399 |  |  |  | -0.12 | 59.88 | 49.88
1400 |  |  |  | -0.12 | 59.88 | 49.88
1401 |  |  |  | -0.12 | 59.88 | 49.88
1402 |  |  |  | -0.12 | 59.88 | 49.88
1403 |  |  |  | -0.12 | 59.88 | 49.88
1404 |  |  |  | -0.12 | 59.88 | 49.88
1405 |  |  |  | -0.12 | 59.88 | 49.88
1406 |  |  |  | -0.12 | 59.88 | 49.88
1407 |  |  |  | -0.12 | 59.88 | 49.88
1408 |  |  |  | -0.12 | 59.88 | 49.88
1409 |  |  |  | -0.12 | 59.88 | 49.88
1410 |  |  |  | -0.12 | 59.88 | 49.88
1411 |  |  |  | -0.12 | 59.88 | 49.88
1412 |  |  |  | -0.12 | 59.88 | 49.88
1413 |  |  |  | -0.12 | 59.88 | 49.88
1414 |  |  |  | -0.12 | 59.88 | 49.88
1415 |  |  |  | -0.12 | 59.88 | 49.88
1416 |  |  |  | -0.12 | 59.88 | 49.88
1417 |  |  |  | -0.12 | 59.88 | 49.88
1418 |  |  |  | -0.12 | 59.88 | 49.88
1419 |  |  |  | -0.12 | 59.88 | 49.88
1420 |  |  |  | -0.12 | 59.88 | 49.88
1421 |  |  |  | -0.12 | 59.88 | 49.88
1422 |  |  |  | -0.12 | 59.88 | 49.88
1423 |  |  |  | -0.12 | 59.88 | 49.88
1424 |  |  |  | -0.12 | 59.88 | 49.88
1425 |  |  |  | -0.12 | 59.88 | 49.88
1426 |  |  |  | -0.12 | 59.88 | 49.88
1427 |  |  |  | -0.12 | 59.88 | 49.88
1428 |  |  |  | -0.12 | 59.88 | 49.88
1429 |  |  |  | -0.12 | 59.88 | 49.88
1430 |  |  |  | -0.12 | 59.88 | 49.88
1431 |  |  |  | -0.12 | 59.88 | 49.88
1432 |  |  |  | -0.12 | 59.88 | 49.88
1433 |  |  |  | -0.12 | 59.88 | 49.88
1434 |  |  |  | -0.12 | 59.88 | 49.88
1435 |  |  |  | -0.12 | 59.88 | 49.88
1436 |  |  |  | -0.12 | 59.88 | 49.88
1437 |  |  |  | -0.12 | 59.88 | 49.88
1438 |  |  |  | -0.12 | 59.88 | 49.88
1439 |  |  |  | -0.12 | 59.88 | 49.88
1440 |  |  |  | -0.12 | 59.88 | 49.88
1441 |  |  |  | -0.12 | 59.88 | 49.88
1442 |  |  |  | -0.12 | 59.88 | 49.88
1443 |  |  |  | -0.12 | 59.88 | 49.88
1444 |  |  |  | -0.12 | 59.88 | 49.88
1445 |  |  |  | -0.12 | 59.88 | 49.88
1446 |  |  |  | -0.12 | 59.88 | 49.88
1447 |  |  |  | -0.12 | 59.88 | 49.88
1448 |  |  |  | -0.12 | 59.88 | 49.88
1449 |  |  |  | -0.12 | 59.88 | 49.88
1450 |  |  |  | -0.12 | 59.88 | 49.88
1451 |  |  |  | -0.12 | 59.88 | 49.88
1452 |  |  |  | -0.12 | 59.88 | 49.88
1453 |  |  |  | -0.12 | 59.88 | 49.88
1454 |  |  |  | -0.12 | 59.88 | 49.88
1455 |  |  |  | -0.12 | 59.88 | 49.88
1456 |  |  |  | -0.12 | 59.88 | 49.88
1457 |  |  |  | -0.12 | 59.88 | 49.88
1458 |  |  |  | -0.12 | 59.88 | 49.88
1459 |  |  |  | -0.12 | 59.88 | 49.88
1460 |  |  |  | -0.12 | 59.88 | 49.88
1461 |  |  |  | -0.12 | 59.88 | 49.88
1462 |  |  |  | -0.12 | 59.88 | 49.88
1463 |  |  |  | -0.12 | 59.88 | 49.88
1464 |  |  |  | -0.12 | 59.88 | 49.88
1465 |  |  |  | -0.12 | 59.88 | 49.88
1466 |  |  |  | -0.12 | 59.88 | 49.88
1467 |  |  |  | -0.12 | 59.88 | 49.88
1468 |  |  |  | -0.12 | 59.88 | 49.88
1469 |  |  |  | -0.12 | 59.88 | 49.88
1470 |  |  |  | -0.12 | 59.88 | 49.88
1471 |  |  |  | -0.12 | 59.88 | 49.88
1472 |  |  |  | -0.12 | 59.88 | 49.88
1473 |  |  |  | -0.12 | 59.88 | 49.88
1474 |  |  |  | -0.12 | 59.88 | 49.88
1475 |  |  |  | -0.12 | 59.88 | 49.88
1476 |  |  |  | -0.12 | 59.88 | 49.88
1477 |  |  |  | -0.12 | 59.88 | 49.88
1478 |  |  |  | -0.12 | 59.88 | 49.88
1479 |  |  |  | -0.12 | 59.88 | 49.88
1480 |  |  |  | -0.12 | 59.88 | 49.88
1481 |  |  |  | -0.12 | 59.88 | 49.88
1482 |  |  |  | -0.12 | 59.88 | 49.88
1483 |  |  |  | -0.12 | 59.88 | 49.88
1484 |  |  |  | -0.12 | 59.88 | 49.88
1485 |  |  |  | -0.12 | 59.88 | 49.88
1486 |  |  |  | -0.12 | 59.88 | 49.88
1487 |  |  |  | -0.12 | 59.88 | 49.88
1488 |  |  |  | -0.12 | 59.88 | 49.88
1489 |  |  |  | -0.12 | 59.88 | 49.88
1490 |  |  |  | -0.12 | 59.88 | 49.88
1491 |  |  |  | -0.12 | 59.88 | 49.88
1492 |  |  |  | -0.12 | 59.88 | 49.88
1493 |  |  |  | -0.12 | 59.88 | 49.88
1494 |  |  |  | -0.12 | 59.88 | 49.88
1495 |  |  |  | -0.12 | 59.88 | 49.88
1496 |  |  |  | -0.12 | 59.88 | 49.88
1497 |  |  |  | -0.12 | 59.88 | 49.88
1498 |  |  |  | -0.12 | 59.88 | 49.88
1499 |  |  |  | -0.12 | 59.88 | 49.88
1500 |  |  |  | 0 | 60 | 50
1501 |  |  |  | 0 | 60 | 50
1502 |  |  |  | 0 | 60 | 50
1503 |  |  |  | 0 | 60 | 50
1504 |  |  |  | 0 | 60 | 50
1505 |  |  |  | 0 | 60 | 50
1506 |  |  |  | 0 | 60 | 50
1507 |  |  |  | 0 | 60 | 50
1508 |  |  |  | 0 | 60 | 50
1509 |  |  |  | 0 | 60 | 50
1510 |  |  |  | 0 | 60 | 50
1511 |  |  |  | 0 | 60 | 50
1512 |  |  |  | 0 | 60 | 50
1513 |  |  |  | 0 | 60 | 50
1514 |  |  |  | 0 | 60 | 50
1515 |  |  |  | 0 | 60 | 50
1516 |  |  |  | 0 | 60 | 50
1517 |  |  |  | 0 | 60 | 50
1518 |  |  |  | 0 | 60 | 50
1519 |  |  |  | 0 | 60 | 50
1520 |  |  |  | 0 | 60 | 50
1521 |  |  |  | 0 | 60 | 50
1522 |  |  |  | 0 | 60 | 50
1523 |  |  |  | 0 | 60 | 50
1524 |  |  |  | 0 | 60 | 50
1525 |  |  |  | 0 | 60 | 50
1526 |  |  |  | 0 | 60 | 50
1527 |  |  |  | 0 | 60 | 50
1528 |  |  |  | 0 | 60 | 50
1529 |  |  |  | 0 | 60 | 50
1530 |  |  |  | 0.16 | 60.16 | 50.16
1531 |  |  |  | 0.16 | 60.16 | 50.16
1532 |  |  |  | 0.16 | 60.16 | 50.16
1533 |  |  |  | 0.16 | 60.16 | 50.16
1534 |  |  |  | 0.16 | 60.16 | 50.16
1535 |  |  |  | 0.16 | 60.16 | 50.16
1536 |  |  |  | 0.16 | 60.16 | 50.16
1537 |  |  |  | 0.16 | 60.16 | 50.16
1538 |  |  |  | 0.16 | 60.16 | 50.16
1539 |  |  |  | 0.16 | 60.16 | 50.16
1540 |  |  |  | 0.16 | 60.16 | 50.16
1541 |  |  |  | 0.16 | 60.16 | 50.16
1542 |  |  |  | 0.16 | 60.16 | 50.16
1543 |  |  |  | 0.16 | 60.16 | 50.16
1544 |  |  |  | 0.16 | 60.16 | 50.16
1545 |  |  |  | 0.16 | 60.16 | 50.16
1546 |  |  |  | 0.16 | 60.16 | 50.16
1547 |  |  |  | 0.16 | 60.16 | 50.16
1548 |  |  |  | 0.16 | 60.16 | 50.16
1549 |  |  |  | 0.16 | 60.16 | 50.16
1550 |  |  |  | 0.16 | 60.16 | 50.16
1551 |  |  |  | 0.16 | 60.16 | 50.16
1552 |  |  |  | 0.16 | 60.16 | 50.16
1553 |  |  |  | 0.16 | 60.16 | 50.16
1554 |  |  |  | 0.16 | 60.16 | 50.16
1555 |  |  |  | 0.16 | 60.16 | 50.16
1556 |  |  |  | 0.16 | 60.16 | 50.16
1557 |  |  |  | 0.16 | 60.16 | 50.16
1558 |  |  |  | 0.16 | 60.16 | 50.16
1559 |  |  |  | 0.16 | 60.16 | 50.16
1560 |  |  |  | 0.16 | 60.16 | 50.16
1561 |  |  |  | 0.16 | 60.16 | 50.16
1562 |  |  |  | 0.16 | 60.16 | 50.16
1563 |  |  |  | 0.16 | 60.16 | 50.16
1564 |  |  |  | 0.16 | 60.16 | 50.16
1565 |  |  |  | 0.16 | 60.16 | 50.16
1566 |  |  |  | 0.16 | 60.16 | 50.16
1567 |  |  |  | 0.16 | 60.16 | 50.16
1568 |  |  |  | 0.16 | 60.16 | 50.16
1569 |  |  |  | 0.16 | 60.16 | 50.16
1570 |  |  |  | 0.16 | 60.16 | 50.16
1571 |  |  |  | 0.16 | 60.16 | 50.16
1572 |  |  |  | 0.16 | 60.16 | 50.16
1573 |  |  |  | 0.16 | 60.16 | 50.16
1574 |  |  |  | 0.16 | 60.16 | 50.16
1575 |  |  |  | 0.16 | 60.16 | 50.16
1576 |  |  |  | 0.16 | 60.16 | 50.16
1577 |  |  |  | 0.16 | 60.16 | 50.16
1578 |  |  |  | 0.16 | 60.16 | 50.16
1579 |  |  |  | 0.16 | 60.16 | 50.16
1580 |  |  |  | 0.16 | 60.16 | 50.16
1581 |  |  |  | 0.16 | 60.16 | 50.16
1582 |  |  |  | 0.16 | 60.16 | 50.16
1583 |  |  |  | 0.16 | 60.16 | 50.16
1584 |  |  |  | 0.16 | 60.16 | 50.16
1585 |  |  |  | 0.16 | 60.16 | 50.16
1586 |  |  |  | 0.16 | 60.16 | 50.16
1587 |  |  |  | 0.16 | 60.16 | 50.16
1588 |  |  |  | 0.16 | 60.16 | 50.16
1589 |  |  |  | 0.16 | 60.16 | 50.16
1590 |  |  |  | 0.16 | 60.16 | 50.16
1591 |  |  |  | 0.16 | 60.16 | 50.16
1592 |  |  |  | 0.16 | 60.16 | 50.16
1593 |  |  |  | 0.16 | 60.16 | 50.16
1594 |  |  |  | 0.16 | 60.16 | 50.16
1595 |  |  |  | 0.16 | 60.16 | 50.16
1596 |  |  |  | 0.16 | 60.16 | 50.16
1597 |  |  |  | 0.16 | 60.16 | 50.16
1598 |  |  |  | 0.16 | 60.16 | 50.16
1599 |  |  |  | 0.16 | 60.16 | 50.16
1600 |  |  |  | 0.16 | 60.16 | 50.16
1601 |  |  |  | 0.16 | 60.16 | 50.16
1602 |  |  |  | 0.16 | 60.16 | 50.16
1603 |  |  |  | 0.16 | 60.16 | 50.16
1604 |  |  |  | 0.16 | 60.16 | 50.16
1605 |  |  |  | 0.16 | 60.16 | 50.16
1606 |  |  |  | 0.16 | 60.16 | 50.16
1607 |  |  |  | 0.16 | 60.16 | 50.16
1608 |  |  |  | 0.16 | 60.16 | 50.16
1609 |  |  |  | 0.16 | 60.16 | 50.16
1610 |  |  |  | 0.16 | 60.16 | 50.16
1611 |  |  |  | 0.16 | 60.16 | 50.16
1612 |  |  |  | 0.16 | 60.16 | 50.16
1613 |  |  |  | 0.16 | 60.16 | 50.16
1614 |  |  |  | 0.16 | 60.16 | 50.16
1615 |  |  |  | 0.16 | 60.16 | 50.16
1616 |  |  |  | 0.16 | 60.16 | 50.16
1617 |  |  |  | 0.16 | 60.16 | 50.16
1618 |  |  |  | 0.16 | 60.16 | 50.16
1619 |  |  |  | 0.16 | 60.16 | 50.16
1620 |  |  |  | 0.16 | 60.16 | 50.16
1621 |  |  |  | 0.16 | 60.16 | 50.16
1622 |  |  |  | 0.16 | 60.16 | 50.16
1623 |  |  |  | 0.16 | 60.16 | 50.16
1624 |  |  |  | 0.16 | 60.16 | 50.16
1625 |  |  |  | 0.16 | 60.16 | 50.16
1626 |  |  |  | 0.16 | 60.16 | 50.16
1627 |  |  |  | 0.16 | 60.16 | 50.16
1628 |  |  |  | 0.16 | 60.16 | 50.16
1629 |  |  |  | 0.16 | 60.16 | 50.16
1630 |  |  |  | 0.16 | 60.16 | 50.16
1631 |  |  |  | 0.16 | 60.16 | 50.16
1632 |  |  |  | 0.16 | 60.16 | 50.16
1633 |  |  |  | 0.16 | 60.16 | 50.16
1634 |  |  |  | 0.16 | 60.16 | 50.16
1635 |  |  |  | 0.16 | 60.16 | 50.16
1636 |  |  |  | 0.16 | 60.16 | 50.16
1637 |  |  |  | 0.16 | 60.16 | 50.16
1638 |  |  |  | 0.16 | 60.16 | 50.16
1639 |  |  |  | 0.16 | 60.16 | 50.16
1640 |  |  |  | 0.16 | 60.16 | 50.16
1641 |  |  |  | 0.16 | 60.16 | 50.16
1642 |  |  |  | 0.16 | 60.16 | 50.16
1643 |  |  |  | 0.16 | 60.16 | 50.16
1644 |  |  |  | 0.16 | 60.16 | 50.16
1645 |  |  |  | 0.16 | 60.16 | 50.16
1646 |  |  |  | 0.16 | 60.16 | 50.16
1647 |  |  |  | 0.16 | 60.16 | 50.16
1648 |  |  |  | 0.16 | 60.16 | 50.16
1649 |  |  |  | 0.16 | 60.16 | 50.16
1650 |  |  |  | 0 | 60 | 50
1651 |  |  |  | 0 | 60 | 50
1652 |  |  |  | 0 | 60 | 50
1653 |  |  |  | 0 | 60 | 50
1654 |  |  |  | 0 | 60 | 50
1655 |  |  |  | 0 | 60 | 50
1656 |  |  |  | 0 | 60 | 50
1657 |  |  |  | 0 | 60 | 50
1658 |  |  |  | 0 | 60 | 50
1659 |  |  |  | 0 | 60 | 50
1660 |  |  |  | 0 | 60 | 50
1661 |  |  |  | 0 | 60 | 50
1662 |  |  |  | 0 | 60 | 50
1663 |  |  |  | 0 | 60 | 50
1664 |  |  |  | 0 | 60 | 50
1665 |  |  |  | 0 | 60 | 50
1666 |  |  |  | 0 | 60 | 50
1667 |  |  |  | 0 | 60 | 50
1668 |  |  |  | 0 | 60 | 50
1669 |  |  |  | 0 | 60 | 50
1670 |  |  |  | 0 | 60 | 50
1671 |  |  |  | 0 | 60 | 50
1672 |  |  |  | 0 | 60 | 50
1673 |  |  |  | 0 | 60 | 50
1674 |  |  |  | 0 | 60 | 50
1675 |  |  |  | 0 | 60 | 50
1676 |  |  |  | 0 | 60 | 50
1677 |  |  |  | 0 | 60 | 50
1678 |  |  |  | 0 | 60 | 50
1679 |  |  |  | 0 | 60 | 50
1680 |  |  |  | -0.16 | 59.84 | 49.84
1681 |  |  |  | -0.16 | 59.84 | 49.84
1682 |  |  |  | -0.16 | 59.84 | 49.84
1683 |  |  |  | -0.16 | 59.84 | 49.84
1684 |  |  |  | -0.16 | 59.84 | 49.84
1685 |  |  |  | -0.16 | 59.84 | 49.84
1686 |  |  |  | -0.16 | 59.84 | 49.84
1687 |  |  |  | -0.16 | 59.84 | 49.84
1688 |  |  |  | -0.16 | 59.84 | 49.84
1689 |  |  |  | -0.16 | 59.84 | 49.84
1690 |  |  |  | -0.16 | 59.84 | 49.84
1691 |  |  |  | -0.16 | 59.84 | 49.84
1692 |  |  |  | -0.16 | 59.84 | 49.84
1693 |  |  |  | -0.16 | 59.84 | 49.84
1694 |  |  |  | -0.16 | 59.84 | 49.84
1695 |  |  |  | -0.16 | 59.84 | 49.84
1696 |  |  |  | -0.16 | 59.84 | 49.84
1697 |  |  |  | -0.16 | 59.84 | 49.84
1698 |  |  |  | -0.16 | 59.84 | 49.84
1699 |  |  |  | -0.16 | 59.84 | 49.84
1700 |  |  |  | -0.16 | 59.84 | 49.84
1701 |  |  |  | -0.16 | 59.84 | 49.84
1702 |  |  |  | -0.16 | 59.84 | 49.84
1703 |  |  |  | -0.16 | 59.84 | 49.84
1704 |  |  |  | -0.16 | 59.84 | 49.84
1705 |  |  |  | -0.16 | 59.84 | 49.84
1706 |  |  |  | -0.16 | 59.84 | 49.84
1707 |  |  |  | -0.16 | 59.84 | 49.84
1708 |  |  |  | -0.16 | 59.84 | 49.84
1709 |  |  |  | -0.16 | 59.84 | 49.84
1710 |  |  |  | -0.16 | 59.84 | 49.84
1711 |  |  |  | -0.16 | 59.84 | 49.84
1712 |  |  |  | -0.16 | 59.84 | 49.84
1713 |  |  |  | -0.16 | 59.84 | 49.84
1714 |  |  |  | -0.16 | 59.84 | 49.84
1715 |  |  |  | -0.16 | 59.84 | 49.84
1716 |  |  |  | -0.16 | 59.84 | 49.84
1717 |  |  |  | -0.16 | 59.84 | 49.84
1718 |  |  |  | -0.16 | 59.84 | 49.84
1719 |  |  |  | -0.16 | 59.84 | 49.84
1720 |  |  |  | -0.16 | 59.84 | 49.84
1721 |  |  |  | -0.16 | 59.84 | 49.84
1722 |  |  |  | -0.16 | 59.84 | 49.84
1723 |  |  |  | -0.16 | 59.84 | 49.84
1724 |  |  |  | -0.16 | 59.84 | 49.84
1725 |  |  |  | -0.16 | 59.84 | 49.84
1726 |  |  |  | -0.16 | 59.84 | 49.84
1727 |  |  |  | -0.16 | 59.84 | 49.84
1728 |  |  |  | -0.16 | 59.84 | 49.84
1729 |  |  |  | -0.16 | 59.84 | 49.84
1730 |  |  |  | -0.16 | 59.84 | 49.84
1731 |  |  |  | -0.16 | 59.84 | 49.84
1732 |  |  |  | -0.16 | 59.84 | 49.84
1733 |  |  |  | -0.16 | 59.84 | 49.84
1734 |  |  |  | -0.16 | 59.84 | 49.84
1735 |  |  |  | -0.16 | 59.84 | 49.84
1736 |  |  |  | -0.16 | 59.84 | 49.84
1737 |  |  |  | -0.16 | 59.84 | 49.84
1738 |  |  |  | -0.16 | 59.84 | 49.84
1739 |  |  |  | -0.16 | 59.84 | 49.84
1740 |  |  |  | -0.16 | 59.84 | 49.84
1741 |  |  |  | -0.16 | 59.84 | 49.84
1742 |  |  |  | -0.16 | 59.84 | 49.84
1743 |  |  |  | -0.16 | 59.84 | 49.84
1744 |  |  |  | -0.16 | 59.84 | 49.84
1745 |  |  |  | -0.16 | 59.84 | 49.84
1746 |  |  |  | -0.16 | 59.84 | 49.84
1747 |  |  |  | -0.16 | 59.84 | 49.84
1748 |  |  |  | -0.16 | 59.84 | 49.84
1749 |  |  |  | -0.16 | 59.84 | 49.84
1750 |  |  |  | -0.16 | 59.84 | 49.84
1751 |  |  |  | -0.16 | 59.84 | 49.84
1752 |  |  |  | -0.16 | 59.84 | 49.84
1753 |  |  |  | -0.16 | 59.84 | 49.84
1754 |  |  |  | -0.16 | 59.84 | 49.84
1755 |  |  |  | -0.16 | 59.84 | 49.84
1756 |  |  |  | -0.16 | 59.84 | 49.84
1757 |  |  |  | -0.16 | 59.84 | 49.84
1758 |  |  |  | -0.16 | 59.84 | 49.84
1759 |  |  |  | -0.16 | 59.84 | 49.84
1760 |  |  |  | -0.16 | 59.84 | 49.84
1761 |  |  |  | -0.16 | 59.84 | 49.84
1762 |  |  |  | -0.16 | 59.84 | 49.84
1763 |  |  |  | -0.16 | 59.84 | 49.84
1764 |  |  |  | -0.16 | 59.84 | 49.84
1765 |  |  |  | -0.16 | 59.84 | 49.84
1766 |  |  |  | -0.16 | 59.84 | 49.84
1767 |  |  |  | -0.16 | 59.84 | 49.84
1768 |  |  |  | -0.16 | 59.84 | 49.84
1769 |  |  |  | -0.16 | 59.84 | 49.84
1770 |  |  |  | -0.16 | 59.84 | 49.84
1771 |  |  |  | -0.16 | 59.84 | 49.84
1772 |  |  |  | -0.16 | 59.84 | 49.84
1773 |  |  |  | -0.16 | 59.84 | 49.84
1774 |  |  |  | -0.16 | 59.84 | 49.84
1775 |  |  |  | -0.16 | 59.84 | 49.84
1776 |  |  |  | -0.16 | 59.84 | 49.84
1777 |  |  |  | -0.16 | 59.84 | 49.84
1778 |  |  |  | -0.16 | 59.84 | 49.84
1779 |  |  |  | -0.16 | 59.84 | 49.84
1780 |  |  |  | -0.16 | 59.84 | 49.84
1781 |  |  |  | -0.16 | 59.84 | 49.84
1782 |  |  |  | -0.16 | 59.84 | 49.84
1783 |  |  |  | -0.16 | 59.84 | 49.84
1784 |  |  |  | -0.16 | 59.84 | 49.84
1785 |  |  |  | -0.16 | 59.84 | 49.84
1786 |  |  |  | -0.16 | 59.84 | 49.84
1787 |  |  |  | -0.16 | 59.84 | 49.84
1788 |  |  |  | -0.16 | 59.84 | 49.84
1789 |  |  |  | -0.16 | 59.84 | 49.84
1790 |  |  |  | -0.16 | 59.84 | 49.84
1791 |  |  |  | -0.16 | 59.84 | 49.84
1792 |  |  |  | -0.16 | 59.84 | 49.84
1793 |  |  |  | -0.16 | 59.84 | 49.84
1794 |  |  |  | -0.16 | 59.84 | 49.84
1795 |  |  |  | -0.16 | 59.84 | 49.84
1796 |  |  |  | -0.16 | 59.84 | 49.84
1797 |  |  |  | -0.16 | 59.84 | 49.84
1798 |  |  |  | -0.16 | 59.84 | 49.84
1799 |  |  |  | -0.16 | 59.84 | 49.84
1800 |  |  |  | 0 | 60 | 50
1801 |  |  |  | 0 | 60 | 50
1802 |  |  |  | 0 | 60 | 50
1803 |  |  |  | 0 | 60 | 50
1804 |  |  |  | 0 | 60 | 50
1805 |  |  |  | 0 | 60 | 50
1806 |  |  |  | 0 | 60 | 50
1807 |  |  |  | 0 | 60 | 50
1808 |  |  |  | 0 | 60 | 50
1809 |  |  |  | 0 | 60 | 50
1810 |  |  |  | 0 | 60 | 50
1811 |  |  |  | 0 | 60 | 50
1812 |  |  |  | 0 | 60 | 50
1813 |  |  |  | 0 | 60 | 50
1814 |  |  |  | 0 | 60 | 50
1815 |  |  |  | 0 | 60 | 50
1816 |  |  |  | 0 | 60 | 50
1817 |  |  |  | 0 | 60 | 50
1818 |  |  |  | 0 | 60 | 50
1819 |  |  |  | 0 | 60 | 50
1820 |  |  |  | 0 | 60 | 50
1821 |  |  |  | 0 | 60 | 50
1822 |  |  |  | 0 | 60 | 50
1823 |  |  |  | 0 | 60 | 50
1824 |  |  |  | 0 | 60 | 50
1825 |  |  |  | 0 | 60 | 50
1826 |  |  |  | 0 | 60 | 50
1827 |  |  |  | 0 | 60 | 50
1828 |  |  |  | 0 | 60 | 50
1829 |  |  |  | 0 | 60 | 50
1830 |  |  |  | 0 | 60 | 50
1831 |  |  |  | 0 | 60 | 50
1832 |  |  |  | 0 | 60 | 50
1833 |  |  |  | 0 | 60 | 50
1834 |  |  |  | 0 | 60 | 50
1835 |  |  |  | 0 | 60 | 50
1836 |  |  |  | 0 | 60 | 50
1837 |  |  |  | 0 | 60 | 50
1838 |  |  |  | 0 | 60 | 50
1839 |  |  |  | 0 | 60 | 50
1840 |  |  |  | 0 | 60 | 50
1841 |  |  |  | 0 | 60 | 50
1842 |  |  |  | 0 | 60 | 50
1843 |  |  |  | 0 | 60 | 50
1844 |  |  |  | 0 | 60 | 50
1845 |  |  |  | 0 | 60 | 50
1846 |  |  |  | 0 | 60 | 50
1847 |  |  |  | 0 | 60 | 50
1848 |  |  |  | 0 | 60 | 50
1849 |  |  |  | 0 | 60 | 50
1850 |  |  |  | 0 | 60 | 50
1851 |  |  |  | 0 | 60 | 50
1852 |  |  |  | 0 | 60 | 50
1853 |  |  |  | 0 | 60 | 50
1854 |  |  |  | 0 | 60 | 50
1855 |  |  |  | 0 | 60 | 50
1856 |  |  |  | 0 | 60 | 50
1857 |  |  |  | 0 | 60 | 50
1858 |  |  |  | 0 | 60 | 50
1859 |  |  |  | 0 | 60 | 50

## 2. Test b not charging
Window start |  | 2026-10-15 | 15:30
Baseline [kW]
Enter the date in the first yellow cell and the start time in the second, then the baseline this window runs on in the third. The Date, Time and Baseline columns fill in for every row.
Window 2 of 3: test b on a NOT CHARGING baseline. Same profile as window 1, different baseline. 1,800 s profile plus a 60 s recovery tail.
Elapsed [s] | Date | Time | Baseline [kW] | Deviation [Hz] | Frequency [Hz] 60 Hz area | Frequency [Hz] 50 Hz area
0 |  |  |  | 0 | 60 | 50
1 |  |  |  | 0 | 60 | 50
2 |  |  |  | 0 | 60 | 50
3 |  |  |  | 0 | 60 | 50
4 |  |  |  | 0 | 60 | 50
5 |  |  |  | 0 | 60 | 50
6 |  |  |  | 0 | 60 | 50
7 |  |  |  | 0 | 60 | 50
8 |  |  |  | 0 | 60 | 50
9 |  |  |  | 0 | 60 | 50
10 |  |  |  | 0 | 60 | 50
11 |  |  |  | 0 | 60 | 50
12 |  |  |  | 0 | 60 | 50
13 |  |  |  | 0 | 60 | 50
14 |  |  |  | 0 | 60 | 50
15 |  |  |  | 0 | 60 | 50
16 |  |  |  | 0 | 60 | 50
17 |  |  |  | 0 | 60 | 50
18 |  |  |  | 0 | 60 | 50
19 |  |  |  | 0 | 60 | 50
20 |  |  |  | 0 | 60 | 50
21 |  |  |  | 0 | 60 | 50
22 |  |  |  | 0 | 60 | 50
23 |  |  |  | 0 | 60 | 50
24 |  |  |  | 0 | 60 | 50
25 |  |  |  | 0 | 60 | 50
26 |  |  |  | 0 | 60 | 50
27 |  |  |  | 0 | 60 | 50
28 |  |  |  | 0 | 60 | 50
29 |  |  |  | 0 | 60 | 50
30 |  |  |  | 0.01 | 60.01 | 50.01
31 |  |  |  | 0.01 | 60.01 | 50.01
32 |  |  |  | 0.01 | 60.01 | 50.01
33 |  |  |  | 0.01 | 60.01 | 50.01
34 |  |  |  | 0.01 | 60.01 | 50.01
35 |  |  |  | 0.01 | 60.01 | 50.01
36 |  |  |  | 0.01 | 60.01 | 50.01
37 |  |  |  | 0.01 | 60.01 | 50.01
38 |  |  |  | 0.01 | 60.01 | 50.01
39 |  |  |  | 0.01 | 60.01 | 50.01
40 |  |  |  | 0.01 | 60.01 | 50.01
41 |  |  |  | 0.01 | 60.01 | 50.01
42 |  |  |  | 0.01 | 60.01 | 50.01
43 |  |  |  | 0.01 | 60.01 | 50.01
44 |  |  |  | 0.01 | 60.01 | 50.01
45 |  |  |  | 0.01 | 60.01 | 50.01
46 |  |  |  | 0.01 | 60.01 | 50.01
47 |  |  |  | 0.01 | 60.01 | 50.01
48 |  |  |  | 0.01 | 60.01 | 50.01
49 |  |  |  | 0.01 | 60.01 | 50.01
50 |  |  |  | 0.01 | 60.01 | 50.01
51 |  |  |  | 0.01 | 60.01 | 50.01
52 |  |  |  | 0.01 | 60.01 | 50.01
53 |  |  |  | 0.01 | 60.01 | 50.01
54 |  |  |  | 0.01 | 60.01 | 50.01
55 |  |  |  | 0.01 | 60.01 | 50.01
56 |  |  |  | 0.01 | 60.01 | 50.01
57 |  |  |  | 0.01 | 60.01 | 50.01
58 |  |  |  | 0.01 | 60.01 | 50.01
59 |  |  |  | 0.01 | 60.01 | 50.01
60 |  |  |  | 0.01 | 60.01 | 50.01
61 |  |  |  | 0.01 | 60.01 | 50.01
62 |  |  |  | 0.01 | 60.01 | 50.01
63 |  |  |  | 0.01 | 60.01 | 50.01
64 |  |  |  | 0.01 | 60.01 | 50.01
65 |  |  |  | 0.01 | 60.01 | 50.01
66 |  |  |  | 0.01 | 60.01 | 50.01
67 |  |  |  | 0.01 | 60.01 | 50.01
68 |  |  |  | 0.01 | 60.01 | 50.01
69 |  |  |  | 0.01 | 60.01 | 50.01
70 |  |  |  | 0.01 | 60.01 | 50.01
71 |  |  |  | 0.01 | 60.01 | 50.01
72 |  |  |  | 0.01 | 60.01 | 50.01
73 |  |  |  | 0.01 | 60.01 | 50.01
74 |  |  |  | 0.01 | 60.01 | 50.01
75 |  |  |  | 0.01 | 60.01 | 50.01
76 |  |  |  | 0.01 | 60.01 | 50.01
77 |  |  |  | 0.01 | 60.01 | 50.01
78 |  |  |  | 0.01 | 60.01 | 50.01
79 |  |  |  | 0.01 | 60.01 | 50.01
80 |  |  |  | 0.01 | 60.01 | 50.01
81 |  |  |  | 0.01 | 60.01 | 50.01
82 |  |  |  | 0.01 | 60.01 | 50.01
83 |  |  |  | 0.01 | 60.01 | 50.01
84 |  |  |  | 0.01 | 60.01 | 50.01
85 |  |  |  | 0.01 | 60.01 | 50.01
86 |  |  |  | 0.01 | 60.01 | 50.01
87 |  |  |  | 0.01 | 60.01 | 50.01
88 |  |  |  | 0.01 | 60.01 | 50.01
89 |  |  |  | 0.01 | 60.01 | 50.01
90 |  |  |  | 0.01 | 60.01 | 50.01
91 |  |  |  | 0.01 | 60.01 | 50.01
92 |  |  |  | 0.01 | 60.01 | 50.01
93 |  |  |  | 0.01 | 60.01 | 50.01
94 |  |  |  | 0.01 | 60.01 | 50.01
95 |  |  |  | 0.01 | 60.01 | 50.01
96 |  |  |  | 0.01 | 60.01 | 50.01
97 |  |  |  | 0.01 | 60.01 | 50.01
98 |  |  |  | 0.01 | 60.01 | 50.01
99 |  |  |  | 0.01 | 60.01 | 50.01
100 |  |  |  | 0.01 | 60.01 | 50.01
101 |  |  |  | 0.01 | 60.01 | 50.01
102 |  |  |  | 0.01 | 60.01 | 50.01
103 |  |  |  | 0.01 | 60.01 | 50.01
104 |  |  |  | 0.01 | 60.01 | 50.01
105 |  |  |  | 0.01 | 60.01 | 50.01
106 |  |  |  | 0.01 | 60.01 | 50.01
107 |  |  |  | 0.01 | 60.01 | 50.01
108 |  |  |  | 0.01 | 60.01 | 50.01
109 |  |  |  | 0.01 | 60.01 | 50.01
110 |  |  |  | 0.01 | 60.01 | 50.01
111 |  |  |  | 0.01 | 60.01 | 50.01
112 |  |  |  | 0.01 | 60.01 | 50.01
113 |  |  |  | 0.01 | 60.01 | 50.01
114 |  |  |  | 0.01 | 60.01 | 50.01
115 |  |  |  | 0.01 | 60.01 | 50.01
116 |  |  |  | 0.01 | 60.01 | 50.01
117 |  |  |  | 0.01 | 60.01 | 50.01
118 |  |  |  | 0.01 | 60.01 | 50.01
119 |  |  |  | 0.01 | 60.01 | 50.01
120 |  |  |  | 0.01 | 60.01 | 50.01
121 |  |  |  | 0.01 | 60.01 | 50.01
122 |  |  |  | 0.01 | 60.01 | 50.01
123 |  |  |  | 0.01 | 60.01 | 50.01
124 |  |  |  | 0.01 | 60.01 | 50.01
125 |  |  |  | 0.01 | 60.01 | 50.01
126 |  |  |  | 0.01 | 60.01 | 50.01
127 |  |  |  | 0.01 | 60.01 | 50.01
128 |  |  |  | 0.01 | 60.01 | 50.01
129 |  |  |  | 0.01 | 60.01 | 50.01
130 |  |  |  | 0.01 | 60.01 | 50.01
131 |  |  |  | 0.01 | 60.01 | 50.01
132 |  |  |  | 0.01 | 60.01 | 50.01
133 |  |  |  | 0.01 | 60.01 | 50.01
134 |  |  |  | 0.01 | 60.01 | 50.01
135 |  |  |  | 0.01 | 60.01 | 50.01
136 |  |  |  | 0.01 | 60.01 | 50.01
137 |  |  |  | 0.01 | 60.01 | 50.01
138 |  |  |  | 0.01 | 60.01 | 50.01
139 |  |  |  | 0.01 | 60.01 | 50.01
140 |  |  |  | 0.01 | 60.01 | 50.01
141 |  |  |  | 0.01 | 60.01 | 50.01
142 |  |  |  | 0.01 | 60.01 | 50.01
143 |  |  |  | 0.01 | 60.01 | 50.01
144 |  |  |  | 0.01 | 60.01 | 50.01
145 |  |  |  | 0.01 | 60.01 | 50.01
146 |  |  |  | 0.01 | 60.01 | 50.01
147 |  |  |  | 0.01 | 60.01 | 50.01
148 |  |  |  | 0.01 | 60.01 | 50.01
149 |  |  |  | 0.01 | 60.01 | 50.01
150 |  |  |  | 0 | 60 | 50
151 |  |  |  | 0 | 60 | 50
152 |  |  |  | 0 | 60 | 50
153 |  |  |  | 0 | 60 | 50
154 |  |  |  | 0 | 60 | 50
155 |  |  |  | 0 | 60 | 50
156 |  |  |  | 0 | 60 | 50
157 |  |  |  | 0 | 60 | 50
158 |  |  |  | 0 | 60 | 50
159 |  |  |  | 0 | 60 | 50
160 |  |  |  | 0 | 60 | 50
161 |  |  |  | 0 | 60 | 50
162 |  |  |  | 0 | 60 | 50
163 |  |  |  | 0 | 60 | 50
164 |  |  |  | 0 | 60 | 50
165 |  |  |  | 0 | 60 | 50
166 |  |  |  | 0 | 60 | 50
167 |  |  |  | 0 | 60 | 50
168 |  |  |  | 0 | 60 | 50
169 |  |  |  | 0 | 60 | 50
170 |  |  |  | 0 | 60 | 50
171 |  |  |  | 0 | 60 | 50
172 |  |  |  | 0 | 60 | 50
173 |  |  |  | 0 | 60 | 50
174 |  |  |  | 0 | 60 | 50
175 |  |  |  | 0 | 60 | 50
176 |  |  |  | 0 | 60 | 50
177 |  |  |  | 0 | 60 | 50
178 |  |  |  | 0 | 60 | 50
179 |  |  |  | 0 | 60 | 50
180 |  |  |  | -0.01 | 59.99 | 49.99
181 |  |  |  | -0.01 | 59.99 | 49.99
182 |  |  |  | -0.01 | 59.99 | 49.99
183 |  |  |  | -0.01 | 59.99 | 49.99
184 |  |  |  | -0.01 | 59.99 | 49.99
185 |  |  |  | -0.01 | 59.99 | 49.99
186 |  |  |  | -0.01 | 59.99 | 49.99
187 |  |  |  | -0.01 | 59.99 | 49.99
188 |  |  |  | -0.01 | 59.99 | 49.99
189 |  |  |  | -0.01 | 59.99 | 49.99
190 |  |  |  | -0.01 | 59.99 | 49.99
191 |  |  |  | -0.01 | 59.99 | 49.99
192 |  |  |  | -0.01 | 59.99 | 49.99
193 |  |  |  | -0.01 | 59.99 | 49.99
194 |  |  |  | -0.01 | 59.99 | 49.99
195 |  |  |  | -0.01 | 59.99 | 49.99
196 |  |  |  | -0.01 | 59.99 | 49.99
197 |  |  |  | -0.01 | 59.99 | 49.99
198 |  |  |  | -0.01 | 59.99 | 49.99
199 |  |  |  | -0.01 | 59.99 | 49.99
200 |  |  |  | -0.01 | 59.99 | 49.99
201 |  |  |  | -0.01 | 59.99 | 49.99
202 |  |  |  | -0.01 | 59.99 | 49.99
203 |  |  |  | -0.01 | 59.99 | 49.99
204 |  |  |  | -0.01 | 59.99 | 49.99
205 |  |  |  | -0.01 | 59.99 | 49.99
206 |  |  |  | -0.01 | 59.99 | 49.99
207 |  |  |  | -0.01 | 59.99 | 49.99
208 |  |  |  | -0.01 | 59.99 | 49.99
209 |  |  |  | -0.01 | 59.99 | 49.99
210 |  |  |  | -0.01 | 59.99 | 49.99
211 |  |  |  | -0.01 | 59.99 | 49.99
212 |  |  |  | -0.01 | 59.99 | 49.99
213 |  |  |  | -0.01 | 59.99 | 49.99
214 |  |  |  | -0.01 | 59.99 | 49.99
215 |  |  |  | -0.01 | 59.99 | 49.99
216 |  |  |  | -0.01 | 59.99 | 49.99
217 |  |  |  | -0.01 | 59.99 | 49.99
218 |  |  |  | -0.01 | 59.99 | 49.99
219 |  |  |  | -0.01 | 59.99 | 49.99
220 |  |  |  | -0.01 | 59.99 | 49.99
221 |  |  |  | -0.01 | 59.99 | 49.99
222 |  |  |  | -0.01 | 59.99 | 49.99
223 |  |  |  | -0.01 | 59.99 | 49.99
224 |  |  |  | -0.01 | 59.99 | 49.99
225 |  |  |  | -0.01 | 59.99 | 49.99
226 |  |  |  | -0.01 | 59.99 | 49.99
227 |  |  |  | -0.01 | 59.99 | 49.99
228 |  |  |  | -0.01 | 59.99 | 49.99
229 |  |  |  | -0.01 | 59.99 | 49.99
230 |  |  |  | -0.01 | 59.99 | 49.99
231 |  |  |  | -0.01 | 59.99 | 49.99
232 |  |  |  | -0.01 | 59.99 | 49.99
233 |  |  |  | -0.01 | 59.99 | 49.99
234 |  |  |  | -0.01 | 59.99 | 49.99
235 |  |  |  | -0.01 | 59.99 | 49.99
236 |  |  |  | -0.01 | 59.99 | 49.99
237 |  |  |  | -0.01 | 59.99 | 49.99
238 |  |  |  | -0.01 | 59.99 | 49.99
239 |  |  |  | -0.01 | 59.99 | 49.99
240 |  |  |  | -0.01 | 59.99 | 49.99
241 |  |  |  | -0.01 | 59.99 | 49.99
242 |  |  |  | -0.01 | 59.99 | 49.99
243 |  |  |  | -0.01 | 59.99 | 49.99
244 |  |  |  | -0.01 | 59.99 | 49.99
245 |  |  |  | -0.01 | 59.99 | 49.99
246 |  |  |  | -0.01 | 59.99 | 49.99
247 |  |  |  | -0.01 | 59.99 | 49.99
248 |  |  |  | -0.01 | 59.99 | 49.99
249 |  |  |  | -0.01 | 59.99 | 49.99
250 |  |  |  | -0.01 | 59.99 | 49.99
251 |  |  |  | -0.01 | 59.99 | 49.99
252 |  |  |  | -0.01 | 59.99 | 49.99
253 |  |  |  | -0.01 | 59.99 | 49.99
254 |  |  |  | -0.01 | 59.99 | 49.99
255 |  |  |  | -0.01 | 59.99 | 49.99
256 |  |  |  | -0.01 | 59.99 | 49.99
257 |  |  |  | -0.01 | 59.99 | 49.99
258 |  |  |  | -0.01 | 59.99 | 49.99
259 |  |  |  | -0.01 | 59.99 | 49.99
260 |  |  |  | -0.01 | 59.99 | 49.99
261 |  |  |  | -0.01 | 59.99 | 49.99
262 |  |  |  | -0.01 | 59.99 | 49.99
263 |  |  |  | -0.01 | 59.99 | 49.99
264 |  |  |  | -0.01 | 59.99 | 49.99
265 |  |  |  | -0.01 | 59.99 | 49.99
266 |  |  |  | -0.01 | 59.99 | 49.99
267 |  |  |  | -0.01 | 59.99 | 49.99
268 |  |  |  | -0.01 | 59.99 | 49.99
269 |  |  |  | -0.01 | 59.99 | 49.99
270 |  |  |  | -0.01 | 59.99 | 49.99
271 |  |  |  | -0.01 | 59.99 | 49.99
272 |  |  |  | -0.01 | 59.99 | 49.99
273 |  |  |  | -0.01 | 59.99 | 49.99
274 |  |  |  | -0.01 | 59.99 | 49.99
275 |  |  |  | -0.01 | 59.99 | 49.99
276 |  |  |  | -0.01 | 59.99 | 49.99
277 |  |  |  | -0.01 | 59.99 | 49.99
278 |  |  |  | -0.01 | 59.99 | 49.99
279 |  |  |  | -0.01 | 59.99 | 49.99
280 |  |  |  | -0.01 | 59.99 | 49.99
281 |  |  |  | -0.01 | 59.99 | 49.99
282 |  |  |  | -0.01 | 59.99 | 49.99
283 |  |  |  | -0.01 | 59.99 | 49.99
284 |  |  |  | -0.01 | 59.99 | 49.99
285 |  |  |  | -0.01 | 59.99 | 49.99
286 |  |  |  | -0.01 | 59.99 | 49.99
287 |  |  |  | -0.01 | 59.99 | 49.99
288 |  |  |  | -0.01 | 59.99 | 49.99
289 |  |  |  | -0.01 | 59.99 | 49.99
290 |  |  |  | -0.01 | 59.99 | 49.99
291 |  |  |  | -0.01 | 59.99 | 49.99
292 |  |  |  | -0.01 | 59.99 | 49.99
293 |  |  |  | -0.01 | 59.99 | 49.99
294 |  |  |  | -0.01 | 59.99 | 49.99
295 |  |  |  | -0.01 | 59.99 | 49.99
296 |  |  |  | -0.01 | 59.99 | 49.99
297 |  |  |  | -0.01 | 59.99 | 49.99
298 |  |  |  | -0.01 | 59.99 | 49.99
299 |  |  |  | -0.01 | 59.99 | 49.99
300 |  |  |  | 0 | 60 | 50
301 |  |  |  | 0 | 60 | 50
302 |  |  |  | 0 | 60 | 50
303 |  |  |  | 0 | 60 | 50
304 |  |  |  | 0 | 60 | 50
305 |  |  |  | 0 | 60 | 50
306 |  |  |  | 0 | 60 | 50
307 |  |  |  | 0 | 60 | 50
308 |  |  |  | 0 | 60 | 50
309 |  |  |  | 0 | 60 | 50
310 |  |  |  | 0 | 60 | 50
311 |  |  |  | 0 | 60 | 50
312 |  |  |  | 0 | 60 | 50
313 |  |  |  | 0 | 60 | 50
314 |  |  |  | 0 | 60 | 50
315 |  |  |  | 0 | 60 | 50
316 |  |  |  | 0 | 60 | 50
317 |  |  |  | 0 | 60 | 50
318 |  |  |  | 0 | 60 | 50
319 |  |  |  | 0 | 60 | 50
320 |  |  |  | 0 | 60 | 50
321 |  |  |  | 0 | 60 | 50
322 |  |  |  | 0 | 60 | 50
323 |  |  |  | 0 | 60 | 50
324 |  |  |  | 0 | 60 | 50
325 |  |  |  | 0 | 60 | 50
326 |  |  |  | 0 | 60 | 50
327 |  |  |  | 0 | 60 | 50
328 |  |  |  | 0 | 60 | 50
329 |  |  |  | 0 | 60 | 50
330 |  |  |  | 0.03 | 60.03 | 50.03
331 |  |  |  | 0.03 | 60.03 | 50.03
332 |  |  |  | 0.03 | 60.03 | 50.03
333 |  |  |  | 0.03 | 60.03 | 50.03
334 |  |  |  | 0.03 | 60.03 | 50.03
335 |  |  |  | 0.03 | 60.03 | 50.03
336 |  |  |  | 0.03 | 60.03 | 50.03
337 |  |  |  | 0.03 | 60.03 | 50.03
338 |  |  |  | 0.03 | 60.03 | 50.03
339 |  |  |  | 0.03 | 60.03 | 50.03
340 |  |  |  | 0.03 | 60.03 | 50.03
341 |  |  |  | 0.03 | 60.03 | 50.03
342 |  |  |  | 0.03 | 60.03 | 50.03
343 |  |  |  | 0.03 | 60.03 | 50.03
344 |  |  |  | 0.03 | 60.03 | 50.03
345 |  |  |  | 0.03 | 60.03 | 50.03
346 |  |  |  | 0.03 | 60.03 | 50.03
347 |  |  |  | 0.03 | 60.03 | 50.03
348 |  |  |  | 0.03 | 60.03 | 50.03
349 |  |  |  | 0.03 | 60.03 | 50.03
350 |  |  |  | 0.03 | 60.03 | 50.03
351 |  |  |  | 0.03 | 60.03 | 50.03
352 |  |  |  | 0.03 | 60.03 | 50.03
353 |  |  |  | 0.03 | 60.03 | 50.03
354 |  |  |  | 0.03 | 60.03 | 50.03
355 |  |  |  | 0.03 | 60.03 | 50.03
356 |  |  |  | 0.03 | 60.03 | 50.03
357 |  |  |  | 0.03 | 60.03 | 50.03
358 |  |  |  | 0.03 | 60.03 | 50.03
359 |  |  |  | 0.03 | 60.03 | 50.03
360 |  |  |  | 0.03 | 60.03 | 50.03
361 |  |  |  | 0.03 | 60.03 | 50.03
362 |  |  |  | 0.03 | 60.03 | 50.03
363 |  |  |  | 0.03 | 60.03 | 50.03
364 |  |  |  | 0.03 | 60.03 | 50.03
365 |  |  |  | 0.03 | 60.03 | 50.03
366 |  |  |  | 0.03 | 60.03 | 50.03
367 |  |  |  | 0.03 | 60.03 | 50.03
368 |  |  |  | 0.03 | 60.03 | 50.03
369 |  |  |  | 0.03 | 60.03 | 50.03
370 |  |  |  | 0.03 | 60.03 | 50.03
371 |  |  |  | 0.03 | 60.03 | 50.03
372 |  |  |  | 0.03 | 60.03 | 50.03
373 |  |  |  | 0.03 | 60.03 | 50.03
374 |  |  |  | 0.03 | 60.03 | 50.03
375 |  |  |  | 0.03 | 60.03 | 50.03
376 |  |  |  | 0.03 | 60.03 | 50.03
377 |  |  |  | 0.03 | 60.03 | 50.03
378 |  |  |  | 0.03 | 60.03 | 50.03
379 |  |  |  | 0.03 | 60.03 | 50.03
380 |  |  |  | 0.03 | 60.03 | 50.03
381 |  |  |  | 0.03 | 60.03 | 50.03
382 |  |  |  | 0.03 | 60.03 | 50.03
383 |  |  |  | 0.03 | 60.03 | 50.03
384 |  |  |  | 0.03 | 60.03 | 50.03
385 |  |  |  | 0.03 | 60.03 | 50.03
386 |  |  |  | 0.03 | 60.03 | 50.03
387 |  |  |  | 0.03 | 60.03 | 50.03
388 |  |  |  | 0.03 | 60.03 | 50.03
389 |  |  |  | 0.03 | 60.03 | 50.03
390 |  |  |  | 0.03 | 60.03 | 50.03
391 |  |  |  | 0.03 | 60.03 | 50.03
392 |  |  |  | 0.03 | 60.03 | 50.03
393 |  |  |  | 0.03 | 60.03 | 50.03
394 |  |  |  | 0.03 | 60.03 | 50.03
395 |  |  |  | 0.03 | 60.03 | 50.03
396 |  |  |  | 0.03 | 60.03 | 50.03
397 |  |  |  | 0.03 | 60.03 | 50.03
398 |  |  |  | 0.03 | 60.03 | 50.03
399 |  |  |  | 0.03 | 60.03 | 50.03
400 |  |  |  | 0.03 | 60.03 | 50.03
401 |  |  |  | 0.03 | 60.03 | 50.03
402 |  |  |  | 0.03 | 60.03 | 50.03
403 |  |  |  | 0.03 | 60.03 | 50.03
404 |  |  |  | 0.03 | 60.03 | 50.03
405 |  |  |  | 0.03 | 60.03 | 50.03
406 |  |  |  | 0.03 | 60.03 | 50.03
407 |  |  |  | 0.03 | 60.03 | 50.03
408 |  |  |  | 0.03 | 60.03 | 50.03
409 |  |  |  | 0.03 | 60.03 | 50.03
410 |  |  |  | 0.03 | 60.03 | 50.03
411 |  |  |  | 0.03 | 60.03 | 50.03
412 |  |  |  | 0.03 | 60.03 | 50.03
413 |  |  |  | 0.03 | 60.03 | 50.03
414 |  |  |  | 0.03 | 60.03 | 50.03
415 |  |  |  | 0.03 | 60.03 | 50.03
416 |  |  |  | 0.03 | 60.03 | 50.03
417 |  |  |  | 0.03 | 60.03 | 50.03
418 |  |  |  | 0.03 | 60.03 | 50.03
419 |  |  |  | 0.03 | 60.03 | 50.03
420 |  |  |  | 0.03 | 60.03 | 50.03
421 |  |  |  | 0.03 | 60.03 | 50.03
422 |  |  |  | 0.03 | 60.03 | 50.03
423 |  |  |  | 0.03 | 60.03 | 50.03
424 |  |  |  | 0.03 | 60.03 | 50.03
425 |  |  |  | 0.03 | 60.03 | 50.03
426 |  |  |  | 0.03 | 60.03 | 50.03
427 |  |  |  | 0.03 | 60.03 | 50.03
428 |  |  |  | 0.03 | 60.03 | 50.03
429 |  |  |  | 0.03 | 60.03 | 50.03
430 |  |  |  | 0.03 | 60.03 | 50.03
431 |  |  |  | 0.03 | 60.03 | 50.03
432 |  |  |  | 0.03 | 60.03 | 50.03
433 |  |  |  | 0.03 | 60.03 | 50.03
434 |  |  |  | 0.03 | 60.03 | 50.03
435 |  |  |  | 0.03 | 60.03 | 50.03
436 |  |  |  | 0.03 | 60.03 | 50.03
437 |  |  |  | 0.03 | 60.03 | 50.03
438 |  |  |  | 0.03 | 60.03 | 50.03
439 |  |  |  | 0.03 | 60.03 | 50.03
440 |  |  |  | 0.03 | 60.03 | 50.03
441 |  |  |  | 0.03 | 60.03 | 50.03
442 |  |  |  | 0.03 | 60.03 | 50.03
443 |  |  |  | 0.03 | 60.03 | 50.03
444 |  |  |  | 0.03 | 60.03 | 50.03
445 |  |  |  | 0.03 | 60.03 | 50.03
446 |  |  |  | 0.03 | 60.03 | 50.03
447 |  |  |  | 0.03 | 60.03 | 50.03
448 |  |  |  | 0.03 | 60.03 | 50.03
449 |  |  |  | 0.03 | 60.03 | 50.03
450 |  |  |  | 0 | 60 | 50
451 |  |  |  | 0 | 60 | 50
452 |  |  |  | 0 | 60 | 50
453 |  |  |  | 0 | 60 | 50
454 |  |  |  | 0 | 60 | 50
455 |  |  |  | 0 | 60 | 50
456 |  |  |  | 0 | 60 | 50
457 |  |  |  | 0 | 60 | 50
458 |  |  |  | 0 | 60 | 50
459 |  |  |  | 0 | 60 | 50
460 |  |  |  | 0 | 60 | 50
461 |  |  |  | 0 | 60 | 50
462 |  |  |  | 0 | 60 | 50
463 |  |  |  | 0 | 60 | 50
464 |  |  |  | 0 | 60 | 50
465 |  |  |  | 0 | 60 | 50
466 |  |  |  | 0 | 60 | 50
467 |  |  |  | 0 | 60 | 50
468 |  |  |  | 0 | 60 | 50
469 |  |  |  | 0 | 60 | 50
470 |  |  |  | 0 | 60 | 50
471 |  |  |  | 0 | 60 | 50
472 |  |  |  | 0 | 60 | 50
473 |  |  |  | 0 | 60 | 50
474 |  |  |  | 0 | 60 | 50
475 |  |  |  | 0 | 60 | 50
476 |  |  |  | 0 | 60 | 50
477 |  |  |  | 0 | 60 | 50
478 |  |  |  | 0 | 60 | 50
479 |  |  |  | 0 | 60 | 50
480 |  |  |  | -0.03 | 59.97 | 49.97
481 |  |  |  | -0.03 | 59.97 | 49.97
482 |  |  |  | -0.03 | 59.97 | 49.97
483 |  |  |  | -0.03 | 59.97 | 49.97
484 |  |  |  | -0.03 | 59.97 | 49.97
485 |  |  |  | -0.03 | 59.97 | 49.97
486 |  |  |  | -0.03 | 59.97 | 49.97
487 |  |  |  | -0.03 | 59.97 | 49.97
488 |  |  |  | -0.03 | 59.97 | 49.97
489 |  |  |  | -0.03 | 59.97 | 49.97
490 |  |  |  | -0.03 | 59.97 | 49.97
491 |  |  |  | -0.03 | 59.97 | 49.97
492 |  |  |  | -0.03 | 59.97 | 49.97
493 |  |  |  | -0.03 | 59.97 | 49.97
494 |  |  |  | -0.03 | 59.97 | 49.97
495 |  |  |  | -0.03 | 59.97 | 49.97
496 |  |  |  | -0.03 | 59.97 | 49.97
497 |  |  |  | -0.03 | 59.97 | 49.97
498 |  |  |  | -0.03 | 59.97 | 49.97
499 |  |  |  | -0.03 | 59.97 | 49.97
500 |  |  |  | -0.03 | 59.97 | 49.97
501 |  |  |  | -0.03 | 59.97 | 49.97
502 |  |  |  | -0.03 | 59.97 | 49.97
503 |  |  |  | -0.03 | 59.97 | 49.97
504 |  |  |  | -0.03 | 59.97 | 49.97
505 |  |  |  | -0.03 | 59.97 | 49.97
506 |  |  |  | -0.03 | 59.97 | 49.97
507 |  |  |  | -0.03 | 59.97 | 49.97
508 |  |  |  | -0.03 | 59.97 | 49.97
509 |  |  |  | -0.03 | 59.97 | 49.97
510 |  |  |  | -0.03 | 59.97 | 49.97
511 |  |  |  | -0.03 | 59.97 | 49.97
512 |  |  |  | -0.03 | 59.97 | 49.97
513 |  |  |  | -0.03 | 59.97 | 49.97
514 |  |  |  | -0.03 | 59.97 | 49.97
515 |  |  |  | -0.03 | 59.97 | 49.97
516 |  |  |  | -0.03 | 59.97 | 49.97
517 |  |  |  | -0.03 | 59.97 | 49.97
518 |  |  |  | -0.03 | 59.97 | 49.97
519 |  |  |  | -0.03 | 59.97 | 49.97
520 |  |  |  | -0.03 | 59.97 | 49.97
521 |  |  |  | -0.03 | 59.97 | 49.97
522 |  |  |  | -0.03 | 59.97 | 49.97
523 |  |  |  | -0.03 | 59.97 | 49.97
524 |  |  |  | -0.03 | 59.97 | 49.97
525 |  |  |  | -0.03 | 59.97 | 49.97
526 |  |  |  | -0.03 | 59.97 | 49.97
527 |  |  |  | -0.03 | 59.97 | 49.97
528 |  |  |  | -0.03 | 59.97 | 49.97
529 |  |  |  | -0.03 | 59.97 | 49.97
530 |  |  |  | -0.03 | 59.97 | 49.97
531 |  |  |  | -0.03 | 59.97 | 49.97
532 |  |  |  | -0.03 | 59.97 | 49.97
533 |  |  |  | -0.03 | 59.97 | 49.97
534 |  |  |  | -0.03 | 59.97 | 49.97
535 |  |  |  | -0.03 | 59.97 | 49.97
536 |  |  |  | -0.03 | 59.97 | 49.97
537 |  |  |  | -0.03 | 59.97 | 49.97
538 |  |  |  | -0.03 | 59.97 | 49.97
539 |  |  |  | -0.03 | 59.97 | 49.97
540 |  |  |  | -0.03 | 59.97 | 49.97
541 |  |  |  | -0.03 | 59.97 | 49.97
542 |  |  |  | -0.03 | 59.97 | 49.97
543 |  |  |  | -0.03 | 59.97 | 49.97
544 |  |  |  | -0.03 | 59.97 | 49.97
545 |  |  |  | -0.03 | 59.97 | 49.97
546 |  |  |  | -0.03 | 59.97 | 49.97
547 |  |  |  | -0.03 | 59.97 | 49.97
548 |  |  |  | -0.03 | 59.97 | 49.97
549 |  |  |  | -0.03 | 59.97 | 49.97
550 |  |  |  | -0.03 | 59.97 | 49.97
551 |  |  |  | -0.03 | 59.97 | 49.97
552 |  |  |  | -0.03 | 59.97 | 49.97
553 |  |  |  | -0.03 | 59.97 | 49.97
554 |  |  |  | -0.03 | 59.97 | 49.97
555 |  |  |  | -0.03 | 59.97 | 49.97
556 |  |  |  | -0.03 | 59.97 | 49.97
557 |  |  |  | -0.03 | 59.97 | 49.97
558 |  |  |  | -0.03 | 59.97 | 49.97
559 |  |  |  | -0.03 | 59.97 | 49.97
560 |  |  |  | -0.03 | 59.97 | 49.97
561 |  |  |  | -0.03 | 59.97 | 49.97
562 |  |  |  | -0.03 | 59.97 | 49.97
563 |  |  |  | -0.03 | 59.97 | 49.97
564 |  |  |  | -0.03 | 59.97 | 49.97
565 |  |  |  | -0.03 | 59.97 | 49.97
566 |  |  |  | -0.03 | 59.97 | 49.97
567 |  |  |  | -0.03 | 59.97 | 49.97
568 |  |  |  | -0.03 | 59.97 | 49.97
569 |  |  |  | -0.03 | 59.97 | 49.97
570 |  |  |  | -0.03 | 59.97 | 49.97
571 |  |  |  | -0.03 | 59.97 | 49.97
572 |  |  |  | -0.03 | 59.97 | 49.97
573 |  |  |  | -0.03 | 59.97 | 49.97
574 |  |  |  | -0.03 | 59.97 | 49.97
575 |  |  |  | -0.03 | 59.97 | 49.97
576 |  |  |  | -0.03 | 59.97 | 49.97
577 |  |  |  | -0.03 | 59.97 | 49.97
578 |  |  |  | -0.03 | 59.97 | 49.97
579 |  |  |  | -0.03 | 59.97 | 49.97
580 |  |  |  | -0.03 | 59.97 | 49.97
581 |  |  |  | -0.03 | 59.97 | 49.97
582 |  |  |  | -0.03 | 59.97 | 49.97
583 |  |  |  | -0.03 | 59.97 | 49.97
584 |  |  |  | -0.03 | 59.97 | 49.97
585 |  |  |  | -0.03 | 59.97 | 49.97
586 |  |  |  | -0.03 | 59.97 | 49.97
587 |  |  |  | -0.03 | 59.97 | 49.97
588 |  |  |  | -0.03 | 59.97 | 49.97
589 |  |  |  | -0.03 | 59.97 | 49.97
590 |  |  |  | -0.03 | 59.97 | 49.97
591 |  |  |  | -0.03 | 59.97 | 49.97
592 |  |  |  | -0.03 | 59.97 | 49.97
593 |  |  |  | -0.03 | 59.97 | 49.97
594 |  |  |  | -0.03 | 59.97 | 49.97
595 |  |  |  | -0.03 | 59.97 | 49.97
596 |  |  |  | -0.03 | 59.97 | 49.97
597 |  |  |  | -0.03 | 59.97 | 49.97
598 |  |  |  | -0.03 | 59.97 | 49.97
599 |  |  |  | -0.03 | 59.97 | 49.97
600 |  |  |  | 0 | 60 | 50
601 |  |  |  | 0 | 60 | 50
602 |  |  |  | 0 | 60 | 50
603 |  |  |  | 0 | 60 | 50
604 |  |  |  | 0 | 60 | 50
605 |  |  |  | 0 | 60 | 50
606 |  |  |  | 0 | 60 | 50
607 |  |  |  | 0 | 60 | 50
608 |  |  |  | 0 | 60 | 50
609 |  |  |  | 0 | 60 | 50
610 |  |  |  | 0 | 60 | 50
611 |  |  |  | 0 | 60 | 50
612 |  |  |  | 0 | 60 | 50
613 |  |  |  | 0 | 60 | 50
614 |  |  |  | 0 | 60 | 50
615 |  |  |  | 0 | 60 | 50
616 |  |  |  | 0 | 60 | 50
617 |  |  |  | 0 | 60 | 50
618 |  |  |  | 0 | 60 | 50
619 |  |  |  | 0 | 60 | 50
620 |  |  |  | 0 | 60 | 50
621 |  |  |  | 0 | 60 | 50
622 |  |  |  | 0 | 60 | 50
623 |  |  |  | 0 | 60 | 50
624 |  |  |  | 0 | 60 | 50
625 |  |  |  | 0 | 60 | 50
626 |  |  |  | 0 | 60 | 50
627 |  |  |  | 0 | 60 | 50
628 |  |  |  | 0 | 60 | 50
629 |  |  |  | 0 | 60 | 50
630 |  |  |  | 0.05 | 60.05 | 50.05
631 |  |  |  | 0.05 | 60.05 | 50.05
632 |  |  |  | 0.05 | 60.05 | 50.05
633 |  |  |  | 0.05 | 60.05 | 50.05
634 |  |  |  | 0.05 | 60.05 | 50.05
635 |  |  |  | 0.05 | 60.05 | 50.05
636 |  |  |  | 0.05 | 60.05 | 50.05
637 |  |  |  | 0.05 | 60.05 | 50.05
638 |  |  |  | 0.05 | 60.05 | 50.05
639 |  |  |  | 0.05 | 60.05 | 50.05
640 |  |  |  | 0.05 | 60.05 | 50.05
641 |  |  |  | 0.05 | 60.05 | 50.05
642 |  |  |  | 0.05 | 60.05 | 50.05
643 |  |  |  | 0.05 | 60.05 | 50.05
644 |  |  |  | 0.05 | 60.05 | 50.05
645 |  |  |  | 0.05 | 60.05 | 50.05
646 |  |  |  | 0.05 | 60.05 | 50.05
647 |  |  |  | 0.05 | 60.05 | 50.05
648 |  |  |  | 0.05 | 60.05 | 50.05
649 |  |  |  | 0.05 | 60.05 | 50.05
650 |  |  |  | 0.05 | 60.05 | 50.05
651 |  |  |  | 0.05 | 60.05 | 50.05
652 |  |  |  | 0.05 | 60.05 | 50.05
653 |  |  |  | 0.05 | 60.05 | 50.05
654 |  |  |  | 0.05 | 60.05 | 50.05
655 |  |  |  | 0.05 | 60.05 | 50.05
656 |  |  |  | 0.05 | 60.05 | 50.05
657 |  |  |  | 0.05 | 60.05 | 50.05
658 |  |  |  | 0.05 | 60.05 | 50.05
659 |  |  |  | 0.05 | 60.05 | 50.05
660 |  |  |  | 0.05 | 60.05 | 50.05
661 |  |  |  | 0.05 | 60.05 | 50.05
662 |  |  |  | 0.05 | 60.05 | 50.05
663 |  |  |  | 0.05 | 60.05 | 50.05
664 |  |  |  | 0.05 | 60.05 | 50.05
665 |  |  |  | 0.05 | 60.05 | 50.05
666 |  |  |  | 0.05 | 60.05 | 50.05
667 |  |  |  | 0.05 | 60.05 | 50.05
668 |  |  |  | 0.05 | 60.05 | 50.05
669 |  |  |  | 0.05 | 60.05 | 50.05
670 |  |  |  | 0.05 | 60.05 | 50.05
671 |  |  |  | 0.05 | 60.05 | 50.05
672 |  |  |  | 0.05 | 60.05 | 50.05
673 |  |  |  | 0.05 | 60.05 | 50.05
674 |  |  |  | 0.05 | 60.05 | 50.05
675 |  |  |  | 0.05 | 60.05 | 50.05
676 |  |  |  | 0.05 | 60.05 | 50.05
677 |  |  |  | 0.05 | 60.05 | 50.05
678 |  |  |  | 0.05 | 60.05 | 50.05
679 |  |  |  | 0.05 | 60.05 | 50.05
680 |  |  |  | 0.05 | 60.05 | 50.05
681 |  |  |  | 0.05 | 60.05 | 50.05
682 |  |  |  | 0.05 | 60.05 | 50.05
683 |  |  |  | 0.05 | 60.05 | 50.05
684 |  |  |  | 0.05 | 60.05 | 50.05
685 |  |  |  | 0.05 | 60.05 | 50.05
686 |  |  |  | 0.05 | 60.05 | 50.05
687 |  |  |  | 0.05 | 60.05 | 50.05
688 |  |  |  | 0.05 | 60.05 | 50.05
689 |  |  |  | 0.05 | 60.05 | 50.05
690 |  |  |  | 0.05 | 60.05 | 50.05
691 |  |  |  | 0.05 | 60.05 | 50.05
692 |  |  |  | 0.05 | 60.05 | 50.05
693 |  |  |  | 0.05 | 60.05 | 50.05
694 |  |  |  | 0.05 | 60.05 | 50.05
695 |  |  |  | 0.05 | 60.05 | 50.05
696 |  |  |  | 0.05 | 60.05 | 50.05
697 |  |  |  | 0.05 | 60.05 | 50.05
698 |  |  |  | 0.05 | 60.05 | 50.05
699 |  |  |  | 0.05 | 60.05 | 50.05
700 |  |  |  | 0.05 | 60.05 | 50.05
701 |  |  |  | 0.05 | 60.05 | 50.05
702 |  |  |  | 0.05 | 60.05 | 50.05
703 |  |  |  | 0.05 | 60.05 | 50.05
704 |  |  |  | 0.05 | 60.05 | 50.05
705 |  |  |  | 0.05 | 60.05 | 50.05
706 |  |  |  | 0.05 | 60.05 | 50.05
707 |  |  |  | 0.05 | 60.05 | 50.05
708 |  |  |  | 0.05 | 60.05 | 50.05
709 |  |  |  | 0.05 | 60.05 | 50.05
710 |  |  |  | 0.05 | 60.05 | 50.05
711 |  |  |  | 0.05 | 60.05 | 50.05
712 |  |  |  | 0.05 | 60.05 | 50.05
713 |  |  |  | 0.05 | 60.05 | 50.05
714 |  |  |  | 0.05 | 60.05 | 50.05
715 |  |  |  | 0.05 | 60.05 | 50.05
716 |  |  |  | 0.05 | 60.05 | 50.05
717 |  |  |  | 0.05 | 60.05 | 50.05
718 |  |  |  | 0.05 | 60.05 | 50.05
719 |  |  |  | 0.05 | 60.05 | 50.05
720 |  |  |  | 0.05 | 60.05 | 50.05
721 |  |  |  | 0.05 | 60.05 | 50.05
722 |  |  |  | 0.05 | 60.05 | 50.05
723 |  |  |  | 0.05 | 60.05 | 50.05
724 |  |  |  | 0.05 | 60.05 | 50.05
725 |  |  |  | 0.05 | 60.05 | 50.05
726 |  |  |  | 0.05 | 60.05 | 50.05
727 |  |  |  | 0.05 | 60.05 | 50.05
728 |  |  |  | 0.05 | 60.05 | 50.05
729 |  |  |  | 0.05 | 60.05 | 50.05
730 |  |  |  | 0.05 | 60.05 | 50.05
731 |  |  |  | 0.05 | 60.05 | 50.05
732 |  |  |  | 0.05 | 60.05 | 50.05
733 |  |  |  | 0.05 | 60.05 | 50.05
734 |  |  |  | 0.05 | 60.05 | 50.05
735 |  |  |  | 0.05 | 60.05 | 50.05
736 |  |  |  | 0.05 | 60.05 | 50.05
737 |  |  |  | 0.05 | 60.05 | 50.05
738 |  |  |  | 0.05 | 60.05 | 50.05
739 |  |  |  | 0.05 | 60.05 | 50.05
740 |  |  |  | 0.05 | 60.05 | 50.05
741 |  |  |  | 0.05 | 60.05 | 50.05
742 |  |  |  | 0.05 | 60.05 | 50.05
743 |  |  |  | 0.05 | 60.05 | 50.05
744 |  |  |  | 0.05 | 60.05 | 50.05
745 |  |  |  | 0.05 | 60.05 | 50.05
746 |  |  |  | 0.05 | 60.05 | 50.05
747 |  |  |  | 0.05 | 60.05 | 50.05
748 |  |  |  | 0.05 | 60.05 | 50.05
749 |  |  |  | 0.05 | 60.05 | 50.05
750 |  |  |  | 0 | 60 | 50
751 |  |  |  | 0 | 60 | 50
752 |  |  |  | 0 | 60 | 50
753 |  |  |  | 0 | 60 | 50
754 |  |  |  | 0 | 60 | 50
755 |  |  |  | 0 | 60 | 50
756 |  |  |  | 0 | 60 | 50
757 |  |  |  | 0 | 60 | 50
758 |  |  |  | 0 | 60 | 50
759 |  |  |  | 0 | 60 | 50
760 |  |  |  | 0 | 60 | 50
761 |  |  |  | 0 | 60 | 50
762 |  |  |  | 0 | 60 | 50
763 |  |  |  | 0 | 60 | 50
764 |  |  |  | 0 | 60 | 50
765 |  |  |  | 0 | 60 | 50
766 |  |  |  | 0 | 60 | 50
767 |  |  |  | 0 | 60 | 50
768 |  |  |  | 0 | 60 | 50
769 |  |  |  | 0 | 60 | 50
770 |  |  |  | 0 | 60 | 50
771 |  |  |  | 0 | 60 | 50
772 |  |  |  | 0 | 60 | 50
773 |  |  |  | 0 | 60 | 50
774 |  |  |  | 0 | 60 | 50
775 |  |  |  | 0 | 60 | 50
776 |  |  |  | 0 | 60 | 50
777 |  |  |  | 0 | 60 | 50
778 |  |  |  | 0 | 60 | 50
779 |  |  |  | 0 | 60 | 50
780 |  |  |  | -0.05 | 59.95 | 49.95
781 |  |  |  | -0.05 | 59.95 | 49.95
782 |  |  |  | -0.05 | 59.95 | 49.95
783 |  |  |  | -0.05 | 59.95 | 49.95
784 |  |  |  | -0.05 | 59.95 | 49.95
785 |  |  |  | -0.05 | 59.95 | 49.95
786 |  |  |  | -0.05 | 59.95 | 49.95
787 |  |  |  | -0.05 | 59.95 | 49.95
788 |  |  |  | -0.05 | 59.95 | 49.95
789 |  |  |  | -0.05 | 59.95 | 49.95
790 |  |  |  | -0.05 | 59.95 | 49.95
791 |  |  |  | -0.05 | 59.95 | 49.95
792 |  |  |  | -0.05 | 59.95 | 49.95
793 |  |  |  | -0.05 | 59.95 | 49.95
794 |  |  |  | -0.05 | 59.95 | 49.95
795 |  |  |  | -0.05 | 59.95 | 49.95
796 |  |  |  | -0.05 | 59.95 | 49.95
797 |  |  |  | -0.05 | 59.95 | 49.95
798 |  |  |  | -0.05 | 59.95 | 49.95
799 |  |  |  | -0.05 | 59.95 | 49.95
800 |  |  |  | -0.05 | 59.95 | 49.95
801 |  |  |  | -0.05 | 59.95 | 49.95
802 |  |  |  | -0.05 | 59.95 | 49.95
803 |  |  |  | -0.05 | 59.95 | 49.95
804 |  |  |  | -0.05 | 59.95 | 49.95
805 |  |  |  | -0.05 | 59.95 | 49.95
806 |  |  |  | -0.05 | 59.95 | 49.95
807 |  |  |  | -0.05 | 59.95 | 49.95
808 |  |  |  | -0.05 | 59.95 | 49.95
809 |  |  |  | -0.05 | 59.95 | 49.95
810 |  |  |  | -0.05 | 59.95 | 49.95
811 |  |  |  | -0.05 | 59.95 | 49.95
812 |  |  |  | -0.05 | 59.95 | 49.95
813 |  |  |  | -0.05 | 59.95 | 49.95
814 |  |  |  | -0.05 | 59.95 | 49.95
815 |  |  |  | -0.05 | 59.95 | 49.95
816 |  |  |  | -0.05 | 59.95 | 49.95
817 |  |  |  | -0.05 | 59.95 | 49.95
818 |  |  |  | -0.05 | 59.95 | 49.95
819 |  |  |  | -0.05 | 59.95 | 49.95
820 |  |  |  | -0.05 | 59.95 | 49.95
821 |  |  |  | -0.05 | 59.95 | 49.95
822 |  |  |  | -0.05 | 59.95 | 49.95
823 |  |  |  | -0.05 | 59.95 | 49.95
824 |  |  |  | -0.05 | 59.95 | 49.95
825 |  |  |  | -0.05 | 59.95 | 49.95
826 |  |  |  | -0.05 | 59.95 | 49.95
827 |  |  |  | -0.05 | 59.95 | 49.95
828 |  |  |  | -0.05 | 59.95 | 49.95
829 |  |  |  | -0.05 | 59.95 | 49.95
830 |  |  |  | -0.05 | 59.95 | 49.95
831 |  |  |  | -0.05 | 59.95 | 49.95
832 |  |  |  | -0.05 | 59.95 | 49.95
833 |  |  |  | -0.05 | 59.95 | 49.95
834 |  |  |  | -0.05 | 59.95 | 49.95
835 |  |  |  | -0.05 | 59.95 | 49.95
836 |  |  |  | -0.05 | 59.95 | 49.95
837 |  |  |  | -0.05 | 59.95 | 49.95
838 |  |  |  | -0.05 | 59.95 | 49.95
839 |  |  |  | -0.05 | 59.95 | 49.95
840 |  |  |  | -0.05 | 59.95 | 49.95
841 |  |  |  | -0.05 | 59.95 | 49.95
842 |  |  |  | -0.05 | 59.95 | 49.95
843 |  |  |  | -0.05 | 59.95 | 49.95
844 |  |  |  | -0.05 | 59.95 | 49.95
845 |  |  |  | -0.05 | 59.95 | 49.95
846 |  |  |  | -0.05 | 59.95 | 49.95
847 |  |  |  | -0.05 | 59.95 | 49.95
848 |  |  |  | -0.05 | 59.95 | 49.95
849 |  |  |  | -0.05 | 59.95 | 49.95
850 |  |  |  | -0.05 | 59.95 | 49.95
851 |  |  |  | -0.05 | 59.95 | 49.95
852 |  |  |  | -0.05 | 59.95 | 49.95
853 |  |  |  | -0.05 | 59.95 | 49.95
854 |  |  |  | -0.05 | 59.95 | 49.95
855 |  |  |  | -0.05 | 59.95 | 49.95
856 |  |  |  | -0.05 | 59.95 | 49.95
857 |  |  |  | -0.05 | 59.95 | 49.95
858 |  |  |  | -0.05 | 59.95 | 49.95
859 |  |  |  | -0.05 | 59.95 | 49.95
860 |  |  |  | -0.05 | 59.95 | 49.95
861 |  |  |  | -0.05 | 59.95 | 49.95
862 |  |  |  | -0.05 | 59.95 | 49.95
863 |  |  |  | -0.05 | 59.95 | 49.95
864 |  |  |  | -0.05 | 59.95 | 49.95
865 |  |  |  | -0.05 | 59.95 | 49.95
866 |  |  |  | -0.05 | 59.95 | 49.95
867 |  |  |  | -0.05 | 59.95 | 49.95
868 |  |  |  | -0.05 | 59.95 | 49.95
869 |  |  |  | -0.05 | 59.95 | 49.95
870 |  |  |  | -0.05 | 59.95 | 49.95
871 |  |  |  | -0.05 | 59.95 | 49.95
872 |  |  |  | -0.05 | 59.95 | 49.95
873 |  |  |  | -0.05 | 59.95 | 49.95
874 |  |  |  | -0.05 | 59.95 | 49.95
875 |  |  |  | -0.05 | 59.95 | 49.95
876 |  |  |  | -0.05 | 59.95 | 49.95
877 |  |  |  | -0.05 | 59.95 | 49.95
878 |  |  |  | -0.05 | 59.95 | 49.95
879 |  |  |  | -0.05 | 59.95 | 49.95
880 |  |  |  | -0.05 | 59.95 | 49.95
881 |  |  |  | -0.05 | 59.95 | 49.95
882 |  |  |  | -0.05 | 59.95 | 49.95
883 |  |  |  | -0.05 | 59.95 | 49.95
884 |  |  |  | -0.05 | 59.95 | 49.95
885 |  |  |  | -0.05 | 59.95 | 49.95
886 |  |  |  | -0.05 | 59.95 | 49.95
887 |  |  |  | -0.05 | 59.95 | 49.95
888 |  |  |  | -0.05 | 59.95 | 49.95
889 |  |  |  | -0.05 | 59.95 | 49.95
890 |  |  |  | -0.05 | 59.95 | 49.95
891 |  |  |  | -0.05 | 59.95 | 49.95
892 |  |  |  | -0.05 | 59.95 | 49.95
893 |  |  |  | -0.05 | 59.95 | 49.95
894 |  |  |  | -0.05 | 59.95 | 49.95
895 |  |  |  | -0.05 | 59.95 | 49.95
896 |  |  |  | -0.05 | 59.95 | 49.95
897 |  |  |  | -0.05 | 59.95 | 49.95
898 |  |  |  | -0.05 | 59.95 | 49.95
899 |  |  |  | -0.05 | 59.95 | 49.95
900 |  |  |  | 0 | 60 | 50
901 |  |  |  | 0 | 60 | 50
902 |  |  |  | 0 | 60 | 50
903 |  |  |  | 0 | 60 | 50
904 |  |  |  | 0 | 60 | 50
905 |  |  |  | 0 | 60 | 50
906 |  |  |  | 0 | 60 | 50
907 |  |  |  | 0 | 60 | 50
908 |  |  |  | 0 | 60 | 50
909 |  |  |  | 0 | 60 | 50
910 |  |  |  | 0 | 60 | 50
911 |  |  |  | 0 | 60 | 50
912 |  |  |  | 0 | 60 | 50
913 |  |  |  | 0 | 60 | 50
914 |  |  |  | 0 | 60 | 50
915 |  |  |  | 0 | 60 | 50
916 |  |  |  | 0 | 60 | 50
917 |  |  |  | 0 | 60 | 50
918 |  |  |  | 0 | 60 | 50
919 |  |  |  | 0 | 60 | 50
920 |  |  |  | 0 | 60 | 50
921 |  |  |  | 0 | 60 | 50
922 |  |  |  | 0 | 60 | 50
923 |  |  |  | 0 | 60 | 50
924 |  |  |  | 0 | 60 | 50
925 |  |  |  | 0 | 60 | 50
926 |  |  |  | 0 | 60 | 50
927 |  |  |  | 0 | 60 | 50
928 |  |  |  | 0 | 60 | 50
929 |  |  |  | 0 | 60 | 50
930 |  |  |  | 0.08 | 60.08 | 50.08
931 |  |  |  | 0.08 | 60.08 | 50.08
932 |  |  |  | 0.08 | 60.08 | 50.08
933 |  |  |  | 0.08 | 60.08 | 50.08
934 |  |  |  | 0.08 | 60.08 | 50.08
935 |  |  |  | 0.08 | 60.08 | 50.08
936 |  |  |  | 0.08 | 60.08 | 50.08
937 |  |  |  | 0.08 | 60.08 | 50.08
938 |  |  |  | 0.08 | 60.08 | 50.08
939 |  |  |  | 0.08 | 60.08 | 50.08
940 |  |  |  | 0.08 | 60.08 | 50.08
941 |  |  |  | 0.08 | 60.08 | 50.08
942 |  |  |  | 0.08 | 60.08 | 50.08
943 |  |  |  | 0.08 | 60.08 | 50.08
944 |  |  |  | 0.08 | 60.08 | 50.08
945 |  |  |  | 0.08 | 60.08 | 50.08
946 |  |  |  | 0.08 | 60.08 | 50.08
947 |  |  |  | 0.08 | 60.08 | 50.08
948 |  |  |  | 0.08 | 60.08 | 50.08
949 |  |  |  | 0.08 | 60.08 | 50.08
950 |  |  |  | 0.08 | 60.08 | 50.08
951 |  |  |  | 0.08 | 60.08 | 50.08
952 |  |  |  | 0.08 | 60.08 | 50.08
953 |  |  |  | 0.08 | 60.08 | 50.08
954 |  |  |  | 0.08 | 60.08 | 50.08
955 |  |  |  | 0.08 | 60.08 | 50.08
956 |  |  |  | 0.08 | 60.08 | 50.08
957 |  |  |  | 0.08 | 60.08 | 50.08
958 |  |  |  | 0.08 | 60.08 | 50.08
959 |  |  |  | 0.08 | 60.08 | 50.08
960 |  |  |  | 0.08 | 60.08 | 50.08
961 |  |  |  | 0.08 | 60.08 | 50.08
962 |  |  |  | 0.08 | 60.08 | 50.08
963 |  |  |  | 0.08 | 60.08 | 50.08
964 |  |  |  | 0.08 | 60.08 | 50.08
965 |  |  |  | 0.08 | 60.08 | 50.08
966 |  |  |  | 0.08 | 60.08 | 50.08
967 |  |  |  | 0.08 | 60.08 | 50.08
968 |  |  |  | 0.08 | 60.08 | 50.08
969 |  |  |  | 0.08 | 60.08 | 50.08
970 |  |  |  | 0.08 | 60.08 | 50.08
971 |  |  |  | 0.08 | 60.08 | 50.08
972 |  |  |  | 0.08 | 60.08 | 50.08
973 |  |  |  | 0.08 | 60.08 | 50.08
974 |  |  |  | 0.08 | 60.08 | 50.08
975 |  |  |  | 0.08 | 60.08 | 50.08
976 |  |  |  | 0.08 | 60.08 | 50.08
977 |  |  |  | 0.08 | 60.08 | 50.08
978 |  |  |  | 0.08 | 60.08 | 50.08
979 |  |  |  | 0.08 | 60.08 | 50.08
980 |  |  |  | 0.08 | 60.08 | 50.08
981 |  |  |  | 0.08 | 60.08 | 50.08
982 |  |  |  | 0.08 | 60.08 | 50.08
983 |  |  |  | 0.08 | 60.08 | 50.08
984 |  |  |  | 0.08 | 60.08 | 50.08
985 |  |  |  | 0.08 | 60.08 | 50.08
986 |  |  |  | 0.08 | 60.08 | 50.08
987 |  |  |  | 0.08 | 60.08 | 50.08
988 |  |  |  | 0.08 | 60.08 | 50.08
989 |  |  |  | 0.08 | 60.08 | 50.08
990 |  |  |  | 0.08 | 60.08 | 50.08
991 |  |  |  | 0.08 | 60.08 | 50.08
992 |  |  |  | 0.08 | 60.08 | 50.08
993 |  |  |  | 0.08 | 60.08 | 50.08
994 |  |  |  | 0.08 | 60.08 | 50.08
995 |  |  |  | 0.08 | 60.08 | 50.08
996 |  |  |  | 0.08 | 60.08 | 50.08
997 |  |  |  | 0.08 | 60.08 | 50.08
998 |  |  |  | 0.08 | 60.08 | 50.08
999 |  |  |  | 0.08 | 60.08 | 50.08
1000 |  |  |  | 0.08 | 60.08 | 50.08
1001 |  |  |  | 0.08 | 60.08 | 50.08
1002 |  |  |  | 0.08 | 60.08 | 50.08
1003 |  |  |  | 0.08 | 60.08 | 50.08
1004 |  |  |  | 0.08 | 60.08 | 50.08
1005 |  |  |  | 0.08 | 60.08 | 50.08
1006 |  |  |  | 0.08 | 60.08 | 50.08
1007 |  |  |  | 0.08 | 60.08 | 50.08
1008 |  |  |  | 0.08 | 60.08 | 50.08
1009 |  |  |  | 0.08 | 60.08 | 50.08
1010 |  |  |  | 0.08 | 60.08 | 50.08
1011 |  |  |  | 0.08 | 60.08 | 50.08
1012 |  |  |  | 0.08 | 60.08 | 50.08
1013 |  |  |  | 0.08 | 60.08 | 50.08
1014 |  |  |  | 0.08 | 60.08 | 50.08
1015 |  |  |  | 0.08 | 60.08 | 50.08
1016 |  |  |  | 0.08 | 60.08 | 50.08
1017 |  |  |  | 0.08 | 60.08 | 50.08
1018 |  |  |  | 0.08 | 60.08 | 50.08
1019 |  |  |  | 0.08 | 60.08 | 50.08
1020 |  |  |  | 0.08 | 60.08 | 50.08
1021 |  |  |  | 0.08 | 60.08 | 50.08
1022 |  |  |  | 0.08 | 60.08 | 50.08
1023 |  |  |  | 0.08 | 60.08 | 50.08
1024 |  |  |  | 0.08 | 60.08 | 50.08
1025 |  |  |  | 0.08 | 60.08 | 50.08
1026 |  |  |  | 0.08 | 60.08 | 50.08
1027 |  |  |  | 0.08 | 60.08 | 50.08
1028 |  |  |  | 0.08 | 60.08 | 50.08
1029 |  |  |  | 0.08 | 60.08 | 50.08
1030 |  |  |  | 0.08 | 60.08 | 50.08
1031 |  |  |  | 0.08 | 60.08 | 50.08
1032 |  |  |  | 0.08 | 60.08 | 50.08
1033 |  |  |  | 0.08 | 60.08 | 50.08
1034 |  |  |  | 0.08 | 60.08 | 50.08
1035 |  |  |  | 0.08 | 60.08 | 50.08
1036 |  |  |  | 0.08 | 60.08 | 50.08
1037 |  |  |  | 0.08 | 60.08 | 50.08
1038 |  |  |  | 0.08 | 60.08 | 50.08
1039 |  |  |  | 0.08 | 60.08 | 50.08
1040 |  |  |  | 0.08 | 60.08 | 50.08
1041 |  |  |  | 0.08 | 60.08 | 50.08
1042 |  |  |  | 0.08 | 60.08 | 50.08
1043 |  |  |  | 0.08 | 60.08 | 50.08
1044 |  |  |  | 0.08 | 60.08 | 50.08
1045 |  |  |  | 0.08 | 60.08 | 50.08
1046 |  |  |  | 0.08 | 60.08 | 50.08
1047 |  |  |  | 0.08 | 60.08 | 50.08
1048 |  |  |  | 0.08 | 60.08 | 50.08
1049 |  |  |  | 0.08 | 60.08 | 50.08
1050 |  |  |  | 0 | 60 | 50
1051 |  |  |  | 0 | 60 | 50
1052 |  |  |  | 0 | 60 | 50
1053 |  |  |  | 0 | 60 | 50
1054 |  |  |  | 0 | 60 | 50
1055 |  |  |  | 0 | 60 | 50
1056 |  |  |  | 0 | 60 | 50
1057 |  |  |  | 0 | 60 | 50
1058 |  |  |  | 0 | 60 | 50
1059 |  |  |  | 0 | 60 | 50
1060 |  |  |  | 0 | 60 | 50
1061 |  |  |  | 0 | 60 | 50
1062 |  |  |  | 0 | 60 | 50
1063 |  |  |  | 0 | 60 | 50
1064 |  |  |  | 0 | 60 | 50
1065 |  |  |  | 0 | 60 | 50
1066 |  |  |  | 0 | 60 | 50
1067 |  |  |  | 0 | 60 | 50
1068 |  |  |  | 0 | 60 | 50
1069 |  |  |  | 0 | 60 | 50
1070 |  |  |  | 0 | 60 | 50
1071 |  |  |  | 0 | 60 | 50
1072 |  |  |  | 0 | 60 | 50
1073 |  |  |  | 0 | 60 | 50
1074 |  |  |  | 0 | 60 | 50
1075 |  |  |  | 0 | 60 | 50
1076 |  |  |  | 0 | 60 | 50
1077 |  |  |  | 0 | 60 | 50
1078 |  |  |  | 0 | 60 | 50
1079 |  |  |  | 0 | 60 | 50
1080 |  |  |  | -0.08 | 59.92 | 49.92
1081 |  |  |  | -0.08 | 59.92 | 49.92
1082 |  |  |  | -0.08 | 59.92 | 49.92
1083 |  |  |  | -0.08 | 59.92 | 49.92
1084 |  |  |  | -0.08 | 59.92 | 49.92
1085 |  |  |  | -0.08 | 59.92 | 49.92
1086 |  |  |  | -0.08 | 59.92 | 49.92
1087 |  |  |  | -0.08 | 59.92 | 49.92
1088 |  |  |  | -0.08 | 59.92 | 49.92
1089 |  |  |  | -0.08 | 59.92 | 49.92
1090 |  |  |  | -0.08 | 59.92 | 49.92
1091 |  |  |  | -0.08 | 59.92 | 49.92
1092 |  |  |  | -0.08 | 59.92 | 49.92
1093 |  |  |  | -0.08 | 59.92 | 49.92
1094 |  |  |  | -0.08 | 59.92 | 49.92
1095 |  |  |  | -0.08 | 59.92 | 49.92
1096 |  |  |  | -0.08 | 59.92 | 49.92
1097 |  |  |  | -0.08 | 59.92 | 49.92
1098 |  |  |  | -0.08 | 59.92 | 49.92
1099 |  |  |  | -0.08 | 59.92 | 49.92
1100 |  |  |  | -0.08 | 59.92 | 49.92
1101 |  |  |  | -0.08 | 59.92 | 49.92
1102 |  |  |  | -0.08 | 59.92 | 49.92
1103 |  |  |  | -0.08 | 59.92 | 49.92
1104 |  |  |  | -0.08 | 59.92 | 49.92
1105 |  |  |  | -0.08 | 59.92 | 49.92
1106 |  |  |  | -0.08 | 59.92 | 49.92
1107 |  |  |  | -0.08 | 59.92 | 49.92
1108 |  |  |  | -0.08 | 59.92 | 49.92
1109 |  |  |  | -0.08 | 59.92 | 49.92
1110 |  |  |  | -0.08 | 59.92 | 49.92
1111 |  |  |  | -0.08 | 59.92 | 49.92
1112 |  |  |  | -0.08 | 59.92 | 49.92
1113 |  |  |  | -0.08 | 59.92 | 49.92
1114 |  |  |  | -0.08 | 59.92 | 49.92
1115 |  |  |  | -0.08 | 59.92 | 49.92
1116 |  |  |  | -0.08 | 59.92 | 49.92
1117 |  |  |  | -0.08 | 59.92 | 49.92
1118 |  |  |  | -0.08 | 59.92 | 49.92
1119 |  |  |  | -0.08 | 59.92 | 49.92
1120 |  |  |  | -0.08 | 59.92 | 49.92
1121 |  |  |  | -0.08 | 59.92 | 49.92
1122 |  |  |  | -0.08 | 59.92 | 49.92
1123 |  |  |  | -0.08 | 59.92 | 49.92
1124 |  |  |  | -0.08 | 59.92 | 49.92
1125 |  |  |  | -0.08 | 59.92 | 49.92
1126 |  |  |  | -0.08 | 59.92 | 49.92
1127 |  |  |  | -0.08 | 59.92 | 49.92
1128 |  |  |  | -0.08 | 59.92 | 49.92
1129 |  |  |  | -0.08 | 59.92 | 49.92
1130 |  |  |  | -0.08 | 59.92 | 49.92
1131 |  |  |  | -0.08 | 59.92 | 49.92
1132 |  |  |  | -0.08 | 59.92 | 49.92
1133 |  |  |  | -0.08 | 59.92 | 49.92
1134 |  |  |  | -0.08 | 59.92 | 49.92
1135 |  |  |  | -0.08 | 59.92 | 49.92
1136 |  |  |  | -0.08 | 59.92 | 49.92
1137 |  |  |  | -0.08 | 59.92 | 49.92
1138 |  |  |  | -0.08 | 59.92 | 49.92
1139 |  |  |  | -0.08 | 59.92 | 49.92
1140 |  |  |  | -0.08 | 59.92 | 49.92
1141 |  |  |  | -0.08 | 59.92 | 49.92
1142 |  |  |  | -0.08 | 59.92 | 49.92
1143 |  |  |  | -0.08 | 59.92 | 49.92
1144 |  |  |  | -0.08 | 59.92 | 49.92
1145 |  |  |  | -0.08 | 59.92 | 49.92
1146 |  |  |  | -0.08 | 59.92 | 49.92
1147 |  |  |  | -0.08 | 59.92 | 49.92
1148 |  |  |  | -0.08 | 59.92 | 49.92
1149 |  |  |  | -0.08 | 59.92 | 49.92
1150 |  |  |  | -0.08 | 59.92 | 49.92
1151 |  |  |  | -0.08 | 59.92 | 49.92
1152 |  |  |  | -0.08 | 59.92 | 49.92
1153 |  |  |  | -0.08 | 59.92 | 49.92
1154 |  |  |  | -0.08 | 59.92 | 49.92
1155 |  |  |  | -0.08 | 59.92 | 49.92
1156 |  |  |  | -0.08 | 59.92 | 49.92
1157 |  |  |  | -0.08 | 59.92 | 49.92
1158 |  |  |  | -0.08 | 59.92 | 49.92
1159 |  |  |  | -0.08 | 59.92 | 49.92
1160 |  |  |  | -0.08 | 59.92 | 49.92
1161 |  |  |  | -0.08 | 59.92 | 49.92
1162 |  |  |  | -0.08 | 59.92 | 49.92
1163 |  |  |  | -0.08 | 59.92 | 49.92
1164 |  |  |  | -0.08 | 59.92 | 49.92
1165 |  |  |  | -0.08 | 59.92 | 49.92
1166 |  |  |  | -0.08 | 59.92 | 49.92
1167 |  |  |  | -0.08 | 59.92 | 49.92
1168 |  |  |  | -0.08 | 59.92 | 49.92
1169 |  |  |  | -0.08 | 59.92 | 49.92
1170 |  |  |  | -0.08 | 59.92 | 49.92
1171 |  |  |  | -0.08 | 59.92 | 49.92
1172 |  |  |  | -0.08 | 59.92 | 49.92
1173 |  |  |  | -0.08 | 59.92 | 49.92
1174 |  |  |  | -0.08 | 59.92 | 49.92
1175 |  |  |  | -0.08 | 59.92 | 49.92
1176 |  |  |  | -0.08 | 59.92 | 49.92
1177 |  |  |  | -0.08 | 59.92 | 49.92
1178 |  |  |  | -0.08 | 59.92 | 49.92
1179 |  |  |  | -0.08 | 59.92 | 49.92
1180 |  |  |  | -0.08 | 59.92 | 49.92
1181 |  |  |  | -0.08 | 59.92 | 49.92
1182 |  |  |  | -0.08 | 59.92 | 49.92
1183 |  |  |  | -0.08 | 59.92 | 49.92
1184 |  |  |  | -0.08 | 59.92 | 49.92
1185 |  |  |  | -0.08 | 59.92 | 49.92
1186 |  |  |  | -0.08 | 59.92 | 49.92
1187 |  |  |  | -0.08 | 59.92 | 49.92
1188 |  |  |  | -0.08 | 59.92 | 49.92
1189 |  |  |  | -0.08 | 59.92 | 49.92
1190 |  |  |  | -0.08 | 59.92 | 49.92
1191 |  |  |  | -0.08 | 59.92 | 49.92
1192 |  |  |  | -0.08 | 59.92 | 49.92
1193 |  |  |  | -0.08 | 59.92 | 49.92
1194 |  |  |  | -0.08 | 59.92 | 49.92
1195 |  |  |  | -0.08 | 59.92 | 49.92
1196 |  |  |  | -0.08 | 59.92 | 49.92
1197 |  |  |  | -0.08 | 59.92 | 49.92
1198 |  |  |  | -0.08 | 59.92 | 49.92
1199 |  |  |  | -0.08 | 59.92 | 49.92
1200 |  |  |  | 0 | 60 | 50
1201 |  |  |  | 0 | 60 | 50
1202 |  |  |  | 0 | 60 | 50
1203 |  |  |  | 0 | 60 | 50
1204 |  |  |  | 0 | 60 | 50
1205 |  |  |  | 0 | 60 | 50
1206 |  |  |  | 0 | 60 | 50
1207 |  |  |  | 0 | 60 | 50
1208 |  |  |  | 0 | 60 | 50
1209 |  |  |  | 0 | 60 | 50
1210 |  |  |  | 0 | 60 | 50
1211 |  |  |  | 0 | 60 | 50
1212 |  |  |  | 0 | 60 | 50
1213 |  |  |  | 0 | 60 | 50
1214 |  |  |  | 0 | 60 | 50
1215 |  |  |  | 0 | 60 | 50
1216 |  |  |  | 0 | 60 | 50
1217 |  |  |  | 0 | 60 | 50
1218 |  |  |  | 0 | 60 | 50
1219 |  |  |  | 0 | 60 | 50
1220 |  |  |  | 0 | 60 | 50
1221 |  |  |  | 0 | 60 | 50
1222 |  |  |  | 0 | 60 | 50
1223 |  |  |  | 0 | 60 | 50
1224 |  |  |  | 0 | 60 | 50
1225 |  |  |  | 0 | 60 | 50
1226 |  |  |  | 0 | 60 | 50
1227 |  |  |  | 0 | 60 | 50
1228 |  |  |  | 0 | 60 | 50
1229 |  |  |  | 0 | 60 | 50
1230 |  |  |  | 0.12 | 60.12 | 50.12
1231 |  |  |  | 0.12 | 60.12 | 50.12
1232 |  |  |  | 0.12 | 60.12 | 50.12
1233 |  |  |  | 0.12 | 60.12 | 50.12
1234 |  |  |  | 0.12 | 60.12 | 50.12
1235 |  |  |  | 0.12 | 60.12 | 50.12
1236 |  |  |  | 0.12 | 60.12 | 50.12
1237 |  |  |  | 0.12 | 60.12 | 50.12
1238 |  |  |  | 0.12 | 60.12 | 50.12
1239 |  |  |  | 0.12 | 60.12 | 50.12
1240 |  |  |  | 0.12 | 60.12 | 50.12
1241 |  |  |  | 0.12 | 60.12 | 50.12
1242 |  |  |  | 0.12 | 60.12 | 50.12
1243 |  |  |  | 0.12 | 60.12 | 50.12
1244 |  |  |  | 0.12 | 60.12 | 50.12
1245 |  |  |  | 0.12 | 60.12 | 50.12
1246 |  |  |  | 0.12 | 60.12 | 50.12
1247 |  |  |  | 0.12 | 60.12 | 50.12
1248 |  |  |  | 0.12 | 60.12 | 50.12
1249 |  |  |  | 0.12 | 60.12 | 50.12
1250 |  |  |  | 0.12 | 60.12 | 50.12
1251 |  |  |  | 0.12 | 60.12 | 50.12
1252 |  |  |  | 0.12 | 60.12 | 50.12
1253 |  |  |  | 0.12 | 60.12 | 50.12
1254 |  |  |  | 0.12 | 60.12 | 50.12
1255 |  |  |  | 0.12 | 60.12 | 50.12
1256 |  |  |  | 0.12 | 60.12 | 50.12
1257 |  |  |  | 0.12 | 60.12 | 50.12
1258 |  |  |  | 0.12 | 60.12 | 50.12
1259 |  |  |  | 0.12 | 60.12 | 50.12
1260 |  |  |  | 0.12 | 60.12 | 50.12
1261 |  |  |  | 0.12 | 60.12 | 50.12
1262 |  |  |  | 0.12 | 60.12 | 50.12
1263 |  |  |  | 0.12 | 60.12 | 50.12
1264 |  |  |  | 0.12 | 60.12 | 50.12
1265 |  |  |  | 0.12 | 60.12 | 50.12
1266 |  |  |  | 0.12 | 60.12 | 50.12
1267 |  |  |  | 0.12 | 60.12 | 50.12
1268 |  |  |  | 0.12 | 60.12 | 50.12
1269 |  |  |  | 0.12 | 60.12 | 50.12
1270 |  |  |  | 0.12 | 60.12 | 50.12
1271 |  |  |  | 0.12 | 60.12 | 50.12
1272 |  |  |  | 0.12 | 60.12 | 50.12
1273 |  |  |  | 0.12 | 60.12 | 50.12
1274 |  |  |  | 0.12 | 60.12 | 50.12
1275 |  |  |  | 0.12 | 60.12 | 50.12
1276 |  |  |  | 0.12 | 60.12 | 50.12
1277 |  |  |  | 0.12 | 60.12 | 50.12
1278 |  |  |  | 0.12 | 60.12 | 50.12
1279 |  |  |  | 0.12 | 60.12 | 50.12
1280 |  |  |  | 0.12 | 60.12 | 50.12
1281 |  |  |  | 0.12 | 60.12 | 50.12
1282 |  |  |  | 0.12 | 60.12 | 50.12
1283 |  |  |  | 0.12 | 60.12 | 50.12
1284 |  |  |  | 0.12 | 60.12 | 50.12
1285 |  |  |  | 0.12 | 60.12 | 50.12
1286 |  |  |  | 0.12 | 60.12 | 50.12
1287 |  |  |  | 0.12 | 60.12 | 50.12
1288 |  |  |  | 0.12 | 60.12 | 50.12
1289 |  |  |  | 0.12 | 60.12 | 50.12
1290 |  |  |  | 0.12 | 60.12 | 50.12
1291 |  |  |  | 0.12 | 60.12 | 50.12
1292 |  |  |  | 0.12 | 60.12 | 50.12
1293 |  |  |  | 0.12 | 60.12 | 50.12
1294 |  |  |  | 0.12 | 60.12 | 50.12
1295 |  |  |  | 0.12 | 60.12 | 50.12
1296 |  |  |  | 0.12 | 60.12 | 50.12
1297 |  |  |  | 0.12 | 60.12 | 50.12
1298 |  |  |  | 0.12 | 60.12 | 50.12
1299 |  |  |  | 0.12 | 60.12 | 50.12
1300 |  |  |  | 0.12 | 60.12 | 50.12
1301 |  |  |  | 0.12 | 60.12 | 50.12
1302 |  |  |  | 0.12 | 60.12 | 50.12
1303 |  |  |  | 0.12 | 60.12 | 50.12
1304 |  |  |  | 0.12 | 60.12 | 50.12
1305 |  |  |  | 0.12 | 60.12 | 50.12
1306 |  |  |  | 0.12 | 60.12 | 50.12
1307 |  |  |  | 0.12 | 60.12 | 50.12
1308 |  |  |  | 0.12 | 60.12 | 50.12
1309 |  |  |  | 0.12 | 60.12 | 50.12
1310 |  |  |  | 0.12 | 60.12 | 50.12
1311 |  |  |  | 0.12 | 60.12 | 50.12
1312 |  |  |  | 0.12 | 60.12 | 50.12
1313 |  |  |  | 0.12 | 60.12 | 50.12
1314 |  |  |  | 0.12 | 60.12 | 50.12
1315 |  |  |  | 0.12 | 60.12 | 50.12
1316 |  |  |  | 0.12 | 60.12 | 50.12
1317 |  |  |  | 0.12 | 60.12 | 50.12
1318 |  |  |  | 0.12 | 60.12 | 50.12
1319 |  |  |  | 0.12 | 60.12 | 50.12
1320 |  |  |  | 0.12 | 60.12 | 50.12
1321 |  |  |  | 0.12 | 60.12 | 50.12
1322 |  |  |  | 0.12 | 60.12 | 50.12
1323 |  |  |  | 0.12 | 60.12 | 50.12
1324 |  |  |  | 0.12 | 60.12 | 50.12
1325 |  |  |  | 0.12 | 60.12 | 50.12
1326 |  |  |  | 0.12 | 60.12 | 50.12
1327 |  |  |  | 0.12 | 60.12 | 50.12
1328 |  |  |  | 0.12 | 60.12 | 50.12
1329 |  |  |  | 0.12 | 60.12 | 50.12
1330 |  |  |  | 0.12 | 60.12 | 50.12
1331 |  |  |  | 0.12 | 60.12 | 50.12
1332 |  |  |  | 0.12 | 60.12 | 50.12
1333 |  |  |  | 0.12 | 60.12 | 50.12
1334 |  |  |  | 0.12 | 60.12 | 50.12
1335 |  |  |  | 0.12 | 60.12 | 50.12
1336 |  |  |  | 0.12 | 60.12 | 50.12
1337 |  |  |  | 0.12 | 60.12 | 50.12
1338 |  |  |  | 0.12 | 60.12 | 50.12
1339 |  |  |  | 0.12 | 60.12 | 50.12
1340 |  |  |  | 0.12 | 60.12 | 50.12
1341 |  |  |  | 0.12 | 60.12 | 50.12
1342 |  |  |  | 0.12 | 60.12 | 50.12
1343 |  |  |  | 0.12 | 60.12 | 50.12
1344 |  |  |  | 0.12 | 60.12 | 50.12
1345 |  |  |  | 0.12 | 60.12 | 50.12
1346 |  |  |  | 0.12 | 60.12 | 50.12
1347 |  |  |  | 0.12 | 60.12 | 50.12
1348 |  |  |  | 0.12 | 60.12 | 50.12
1349 |  |  |  | 0.12 | 60.12 | 50.12
1350 |  |  |  | 0 | 60 | 50
1351 |  |  |  | 0 | 60 | 50
1352 |  |  |  | 0 | 60 | 50
1353 |  |  |  | 0 | 60 | 50
1354 |  |  |  | 0 | 60 | 50
1355 |  |  |  | 0 | 60 | 50
1356 |  |  |  | 0 | 60 | 50
1357 |  |  |  | 0 | 60 | 50
1358 |  |  |  | 0 | 60 | 50
1359 |  |  |  | 0 | 60 | 50
1360 |  |  |  | 0 | 60 | 50
1361 |  |  |  | 0 | 60 | 50
1362 |  |  |  | 0 | 60 | 50
1363 |  |  |  | 0 | 60 | 50
1364 |  |  |  | 0 | 60 | 50
1365 |  |  |  | 0 | 60 | 50
1366 |  |  |  | 0 | 60 | 50
1367 |  |  |  | 0 | 60 | 50
1368 |  |  |  | 0 | 60 | 50
1369 |  |  |  | 0 | 60 | 50
1370 |  |  |  | 0 | 60 | 50
1371 |  |  |  | 0 | 60 | 50
1372 |  |  |  | 0 | 60 | 50
1373 |  |  |  | 0 | 60 | 50
1374 |  |  |  | 0 | 60 | 50
1375 |  |  |  | 0 | 60 | 50
1376 |  |  |  | 0 | 60 | 50
1377 |  |  |  | 0 | 60 | 50
1378 |  |  |  | 0 | 60 | 50
1379 |  |  |  | 0 | 60 | 50
1380 |  |  |  | -0.12 | 59.88 | 49.88
1381 |  |  |  | -0.12 | 59.88 | 49.88
1382 |  |  |  | -0.12 | 59.88 | 49.88
1383 |  |  |  | -0.12 | 59.88 | 49.88
1384 |  |  |  | -0.12 | 59.88 | 49.88
1385 |  |  |  | -0.12 | 59.88 | 49.88
1386 |  |  |  | -0.12 | 59.88 | 49.88
1387 |  |  |  | -0.12 | 59.88 | 49.88
1388 |  |  |  | -0.12 | 59.88 | 49.88
1389 |  |  |  | -0.12 | 59.88 | 49.88
1390 |  |  |  | -0.12 | 59.88 | 49.88
1391 |  |  |  | -0.12 | 59.88 | 49.88
1392 |  |  |  | -0.12 | 59.88 | 49.88
1393 |  |  |  | -0.12 | 59.88 | 49.88
1394 |  |  |  | -0.12 | 59.88 | 49.88
1395 |  |  |  | -0.12 | 59.88 | 49.88
1396 |  |  |  | -0.12 | 59.88 | 49.88
1397 |  |  |  | -0.12 | 59.88 | 49.88
1398 |  |  |  | -0.12 | 59.88 | 49.88
1399 |  |  |  | -0.12 | 59.88 | 49.88
1400 |  |  |  | -0.12 | 59.88 | 49.88
1401 |  |  |  | -0.12 | 59.88 | 49.88
1402 |  |  |  | -0.12 | 59.88 | 49.88
1403 |  |  |  | -0.12 | 59.88 | 49.88
1404 |  |  |  | -0.12 | 59.88 | 49.88
1405 |  |  |  | -0.12 | 59.88 | 49.88
1406 |  |  |  | -0.12 | 59.88 | 49.88
1407 |  |  |  | -0.12 | 59.88 | 49.88
1408 |  |  |  | -0.12 | 59.88 | 49.88
1409 |  |  |  | -0.12 | 59.88 | 49.88
1410 |  |  |  | -0.12 | 59.88 | 49.88
1411 |  |  |  | -0.12 | 59.88 | 49.88
1412 |  |  |  | -0.12 | 59.88 | 49.88
1413 |  |  |  | -0.12 | 59.88 | 49.88
1414 |  |  |  | -0.12 | 59.88 | 49.88
1415 |  |  |  | -0.12 | 59.88 | 49.88
1416 |  |  |  | -0.12 | 59.88 | 49.88
1417 |  |  |  | -0.12 | 59.88 | 49.88
1418 |  |  |  | -0.12 | 59.88 | 49.88
1419 |  |  |  | -0.12 | 59.88 | 49.88
1420 |  |  |  | -0.12 | 59.88 | 49.88
1421 |  |  |  | -0.12 | 59.88 | 49.88
1422 |  |  |  | -0.12 | 59.88 | 49.88
1423 |  |  |  | -0.12 | 59.88 | 49.88
1424 |  |  |  | -0.12 | 59.88 | 49.88
1425 |  |  |  | -0.12 | 59.88 | 49.88
1426 |  |  |  | -0.12 | 59.88 | 49.88
1427 |  |  |  | -0.12 | 59.88 | 49.88
1428 |  |  |  | -0.12 | 59.88 | 49.88
1429 |  |  |  | -0.12 | 59.88 | 49.88
1430 |  |  |  | -0.12 | 59.88 | 49.88
1431 |  |  |  | -0.12 | 59.88 | 49.88
1432 |  |  |  | -0.12 | 59.88 | 49.88
1433 |  |  |  | -0.12 | 59.88 | 49.88
1434 |  |  |  | -0.12 | 59.88 | 49.88
1435 |  |  |  | -0.12 | 59.88 | 49.88
1436 |  |  |  | -0.12 | 59.88 | 49.88
1437 |  |  |  | -0.12 | 59.88 | 49.88
1438 |  |  |  | -0.12 | 59.88 | 49.88
1439 |  |  |  | -0.12 | 59.88 | 49.88
1440 |  |  |  | -0.12 | 59.88 | 49.88
1441 |  |  |  | -0.12 | 59.88 | 49.88
1442 |  |  |  | -0.12 | 59.88 | 49.88
1443 |  |  |  | -0.12 | 59.88 | 49.88
1444 |  |  |  | -0.12 | 59.88 | 49.88
1445 |  |  |  | -0.12 | 59.88 | 49.88
1446 |  |  |  | -0.12 | 59.88 | 49.88
1447 |  |  |  | -0.12 | 59.88 | 49.88
1448 |  |  |  | -0.12 | 59.88 | 49.88
1449 |  |  |  | -0.12 | 59.88 | 49.88
1450 |  |  |  | -0.12 | 59.88 | 49.88
1451 |  |  |  | -0.12 | 59.88 | 49.88
1452 |  |  |  | -0.12 | 59.88 | 49.88
1453 |  |  |  | -0.12 | 59.88 | 49.88
1454 |  |  |  | -0.12 | 59.88 | 49.88
1455 |  |  |  | -0.12 | 59.88 | 49.88
1456 |  |  |  | -0.12 | 59.88 | 49.88
1457 |  |  |  | -0.12 | 59.88 | 49.88
1458 |  |  |  | -0.12 | 59.88 | 49.88
1459 |  |  |  | -0.12 | 59.88 | 49.88
1460 |  |  |  | -0.12 | 59.88 | 49.88
1461 |  |  |  | -0.12 | 59.88 | 49.88
1462 |  |  |  | -0.12 | 59.88 | 49.88
1463 |  |  |  | -0.12 | 59.88 | 49.88
1464 |  |  |  | -0.12 | 59.88 | 49.88
1465 |  |  |  | -0.12 | 59.88 | 49.88
1466 |  |  |  | -0.12 | 59.88 | 49.88
1467 |  |  |  | -0.12 | 59.88 | 49.88
1468 |  |  |  | -0.12 | 59.88 | 49.88
1469 |  |  |  | -0.12 | 59.88 | 49.88
1470 |  |  |  | -0.12 | 59.88 | 49.88
1471 |  |  |  | -0.12 | 59.88 | 49.88
1472 |  |  |  | -0.12 | 59.88 | 49.88
1473 |  |  |  | -0.12 | 59.88 | 49.88
1474 |  |  |  | -0.12 | 59.88 | 49.88
1475 |  |  |  | -0.12 | 59.88 | 49.88
1476 |  |  |  | -0.12 | 59.88 | 49.88
1477 |  |  |  | -0.12 | 59.88 | 49.88
1478 |  |  |  | -0.12 | 59.88 | 49.88
1479 |  |  |  | -0.12 | 59.88 | 49.88
1480 |  |  |  | -0.12 | 59.88 | 49.88
1481 |  |  |  | -0.12 | 59.88 | 49.88
1482 |  |  |  | -0.12 | 59.88 | 49.88
1483 |  |  |  | -0.12 | 59.88 | 49.88
1484 |  |  |  | -0.12 | 59.88 | 49.88
1485 |  |  |  | -0.12 | 59.88 | 49.88
1486 |  |  |  | -0.12 | 59.88 | 49.88
1487 |  |  |  | -0.12 | 59.88 | 49.88
1488 |  |  |  | -0.12 | 59.88 | 49.88
1489 |  |  |  | -0.12 | 59.88 | 49.88
1490 |  |  |  | -0.12 | 59.88 | 49.88
1491 |  |  |  | -0.12 | 59.88 | 49.88
1492 |  |  |  | -0.12 | 59.88 | 49.88
1493 |  |  |  | -0.12 | 59.88 | 49.88
1494 |  |  |  | -0.12 | 59.88 | 49.88
1495 |  |  |  | -0.12 | 59.88 | 49.88
1496 |  |  |  | -0.12 | 59.88 | 49.88
1497 |  |  |  | -0.12 | 59.88 | 49.88
1498 |  |  |  | -0.12 | 59.88 | 49.88
1499 |  |  |  | -0.12 | 59.88 | 49.88
1500 |  |  |  | 0 | 60 | 50
1501 |  |  |  | 0 | 60 | 50
1502 |  |  |  | 0 | 60 | 50
1503 |  |  |  | 0 | 60 | 50
1504 |  |  |  | 0 | 60 | 50
1505 |  |  |  | 0 | 60 | 50
1506 |  |  |  | 0 | 60 | 50
1507 |  |  |  | 0 | 60 | 50
1508 |  |  |  | 0 | 60 | 50
1509 |  |  |  | 0 | 60 | 50
1510 |  |  |  | 0 | 60 | 50
1511 |  |  |  | 0 | 60 | 50
1512 |  |  |  | 0 | 60 | 50
1513 |  |  |  | 0 | 60 | 50
1514 |  |  |  | 0 | 60 | 50
1515 |  |  |  | 0 | 60 | 50
1516 |  |  |  | 0 | 60 | 50
1517 |  |  |  | 0 | 60 | 50
1518 |  |  |  | 0 | 60 | 50
1519 |  |  |  | 0 | 60 | 50
1520 |  |  |  | 0 | 60 | 50
1521 |  |  |  | 0 | 60 | 50
1522 |  |  |  | 0 | 60 | 50
1523 |  |  |  | 0 | 60 | 50
1524 |  |  |  | 0 | 60 | 50
1525 |  |  |  | 0 | 60 | 50
1526 |  |  |  | 0 | 60 | 50
1527 |  |  |  | 0 | 60 | 50
1528 |  |  |  | 0 | 60 | 50
1529 |  |  |  | 0 | 60 | 50
1530 |  |  |  | 0.16 | 60.16 | 50.16
1531 |  |  |  | 0.16 | 60.16 | 50.16
1532 |  |  |  | 0.16 | 60.16 | 50.16
1533 |  |  |  | 0.16 | 60.16 | 50.16
1534 |  |  |  | 0.16 | 60.16 | 50.16
1535 |  |  |  | 0.16 | 60.16 | 50.16
1536 |  |  |  | 0.16 | 60.16 | 50.16
1537 |  |  |  | 0.16 | 60.16 | 50.16
1538 |  |  |  | 0.16 | 60.16 | 50.16
1539 |  |  |  | 0.16 | 60.16 | 50.16
1540 |  |  |  | 0.16 | 60.16 | 50.16
1541 |  |  |  | 0.16 | 60.16 | 50.16
1542 |  |  |  | 0.16 | 60.16 | 50.16
1543 |  |  |  | 0.16 | 60.16 | 50.16
1544 |  |  |  | 0.16 | 60.16 | 50.16
1545 |  |  |  | 0.16 | 60.16 | 50.16
1546 |  |  |  | 0.16 | 60.16 | 50.16
1547 |  |  |  | 0.16 | 60.16 | 50.16
1548 |  |  |  | 0.16 | 60.16 | 50.16
1549 |  |  |  | 0.16 | 60.16 | 50.16
1550 |  |  |  | 0.16 | 60.16 | 50.16
1551 |  |  |  | 0.16 | 60.16 | 50.16
1552 |  |  |  | 0.16 | 60.16 | 50.16
1553 |  |  |  | 0.16 | 60.16 | 50.16
1554 |  |  |  | 0.16 | 60.16 | 50.16
1555 |  |  |  | 0.16 | 60.16 | 50.16
1556 |  |  |  | 0.16 | 60.16 | 50.16
1557 |  |  |  | 0.16 | 60.16 | 50.16
1558 |  |  |  | 0.16 | 60.16 | 50.16
1559 |  |  |  | 0.16 | 60.16 | 50.16
1560 |  |  |  | 0.16 | 60.16 | 50.16
1561 |  |  |  | 0.16 | 60.16 | 50.16
1562 |  |  |  | 0.16 | 60.16 | 50.16
1563 |  |  |  | 0.16 | 60.16 | 50.16
1564 |  |  |  | 0.16 | 60.16 | 50.16
1565 |  |  |  | 0.16 | 60.16 | 50.16
1566 |  |  |  | 0.16 | 60.16 | 50.16
1567 |  |  |  | 0.16 | 60.16 | 50.16
1568 |  |  |  | 0.16 | 60.16 | 50.16
1569 |  |  |  | 0.16 | 60.16 | 50.16
1570 |  |  |  | 0.16 | 60.16 | 50.16
1571 |  |  |  | 0.16 | 60.16 | 50.16
1572 |  |  |  | 0.16 | 60.16 | 50.16
1573 |  |  |  | 0.16 | 60.16 | 50.16
1574 |  |  |  | 0.16 | 60.16 | 50.16
1575 |  |  |  | 0.16 | 60.16 | 50.16
1576 |  |  |  | 0.16 | 60.16 | 50.16
1577 |  |  |  | 0.16 | 60.16 | 50.16
1578 |  |  |  | 0.16 | 60.16 | 50.16
1579 |  |  |  | 0.16 | 60.16 | 50.16
1580 |  |  |  | 0.16 | 60.16 | 50.16
1581 |  |  |  | 0.16 | 60.16 | 50.16
1582 |  |  |  | 0.16 | 60.16 | 50.16
1583 |  |  |  | 0.16 | 60.16 | 50.16
1584 |  |  |  | 0.16 | 60.16 | 50.16
1585 |  |  |  | 0.16 | 60.16 | 50.16
1586 |  |  |  | 0.16 | 60.16 | 50.16
1587 |  |  |  | 0.16 | 60.16 | 50.16
1588 |  |  |  | 0.16 | 60.16 | 50.16
1589 |  |  |  | 0.16 | 60.16 | 50.16
1590 |  |  |  | 0.16 | 60.16 | 50.16
1591 |  |  |  | 0.16 | 60.16 | 50.16
1592 |  |  |  | 0.16 | 60.16 | 50.16
1593 |  |  |  | 0.16 | 60.16 | 50.16
1594 |  |  |  | 0.16 | 60.16 | 50.16
1595 |  |  |  | 0.16 | 60.16 | 50.16
1596 |  |  |  | 0.16 | 60.16 | 50.16
1597 |  |  |  | 0.16 | 60.16 | 50.16
1598 |  |  |  | 0.16 | 60.16 | 50.16
1599 |  |  |  | 0.16 | 60.16 | 50.16
1600 |  |  |  | 0.16 | 60.16 | 50.16
1601 |  |  |  | 0.16 | 60.16 | 50.16
1602 |  |  |  | 0.16 | 60.16 | 50.16
1603 |  |  |  | 0.16 | 60.16 | 50.16
1604 |  |  |  | 0.16 | 60.16 | 50.16
1605 |  |  |  | 0.16 | 60.16 | 50.16
1606 |  |  |  | 0.16 | 60.16 | 50.16
1607 |  |  |  | 0.16 | 60.16 | 50.16
1608 |  |  |  | 0.16 | 60.16 | 50.16
1609 |  |  |  | 0.16 | 60.16 | 50.16
1610 |  |  |  | 0.16 | 60.16 | 50.16
1611 |  |  |  | 0.16 | 60.16 | 50.16
1612 |  |  |  | 0.16 | 60.16 | 50.16
1613 |  |  |  | 0.16 | 60.16 | 50.16
1614 |  |  |  | 0.16 | 60.16 | 50.16
1615 |  |  |  | 0.16 | 60.16 | 50.16
1616 |  |  |  | 0.16 | 60.16 | 50.16
1617 |  |  |  | 0.16 | 60.16 | 50.16
1618 |  |  |  | 0.16 | 60.16 | 50.16
1619 |  |  |  | 0.16 | 60.16 | 50.16
1620 |  |  |  | 0.16 | 60.16 | 50.16
1621 |  |  |  | 0.16 | 60.16 | 50.16
1622 |  |  |  | 0.16 | 60.16 | 50.16
1623 |  |  |  | 0.16 | 60.16 | 50.16
1624 |  |  |  | 0.16 | 60.16 | 50.16
1625 |  |  |  | 0.16 | 60.16 | 50.16
1626 |  |  |  | 0.16 | 60.16 | 50.16
1627 |  |  |  | 0.16 | 60.16 | 50.16
1628 |  |  |  | 0.16 | 60.16 | 50.16
1629 |  |  |  | 0.16 | 60.16 | 50.16
1630 |  |  |  | 0.16 | 60.16 | 50.16
1631 |  |  |  | 0.16 | 60.16 | 50.16
1632 |  |  |  | 0.16 | 60.16 | 50.16
1633 |  |  |  | 0.16 | 60.16 | 50.16
1634 |  |  |  | 0.16 | 60.16 | 50.16
1635 |  |  |  | 0.16 | 60.16 | 50.16
1636 |  |  |  | 0.16 | 60.16 | 50.16
1637 |  |  |  | 0.16 | 60.16 | 50.16
1638 |  |  |  | 0.16 | 60.16 | 50.16
1639 |  |  |  | 0.16 | 60.16 | 50.16
1640 |  |  |  | 0.16 | 60.16 | 50.16
1641 |  |  |  | 0.16 | 60.16 | 50.16
1642 |  |  |  | 0.16 | 60.16 | 50.16
1643 |  |  |  | 0.16 | 60.16 | 50.16
1644 |  |  |  | 0.16 | 60.16 | 50.16
1645 |  |  |  | 0.16 | 60.16 | 50.16
1646 |  |  |  | 0.16 | 60.16 | 50.16
1647 |  |  |  | 0.16 | 60.16 | 50.16
1648 |  |  |  | 0.16 | 60.16 | 50.16
1649 |  |  |  | 0.16 | 60.16 | 50.16
1650 |  |  |  | 0 | 60 | 50
1651 |  |  |  | 0 | 60 | 50
1652 |  |  |  | 0 | 60 | 50
1653 |  |  |  | 0 | 60 | 50
1654 |  |  |  | 0 | 60 | 50
1655 |  |  |  | 0 | 60 | 50
1656 |  |  |  | 0 | 60 | 50
1657 |  |  |  | 0 | 60 | 50
1658 |  |  |  | 0 | 60 | 50
1659 |  |  |  | 0 | 60 | 50
1660 |  |  |  | 0 | 60 | 50
1661 |  |  |  | 0 | 60 | 50
1662 |  |  |  | 0 | 60 | 50
1663 |  |  |  | 0 | 60 | 50
1664 |  |  |  | 0 | 60 | 50
1665 |  |  |  | 0 | 60 | 50
1666 |  |  |  | 0 | 60 | 50
1667 |  |  |  | 0 | 60 | 50
1668 |  |  |  | 0 | 60 | 50
1669 |  |  |  | 0 | 60 | 50
1670 |  |  |  | 0 | 60 | 50
1671 |  |  |  | 0 | 60 | 50
1672 |  |  |  | 0 | 60 | 50
1673 |  |  |  | 0 | 60 | 50
1674 |  |  |  | 0 | 60 | 50
1675 |  |  |  | 0 | 60 | 50
1676 |  |  |  | 0 | 60 | 50
1677 |  |  |  | 0 | 60 | 50
1678 |  |  |  | 0 | 60 | 50
1679 |  |  |  | 0 | 60 | 50
1680 |  |  |  | -0.16 | 59.84 | 49.84
1681 |  |  |  | -0.16 | 59.84 | 49.84
1682 |  |  |  | -0.16 | 59.84 | 49.84
1683 |  |  |  | -0.16 | 59.84 | 49.84
1684 |  |  |  | -0.16 | 59.84 | 49.84
1685 |  |  |  | -0.16 | 59.84 | 49.84
1686 |  |  |  | -0.16 | 59.84 | 49.84
1687 |  |  |  | -0.16 | 59.84 | 49.84
1688 |  |  |  | -0.16 | 59.84 | 49.84
1689 |  |  |  | -0.16 | 59.84 | 49.84
1690 |  |  |  | -0.16 | 59.84 | 49.84
1691 |  |  |  | -0.16 | 59.84 | 49.84
1692 |  |  |  | -0.16 | 59.84 | 49.84
1693 |  |  |  | -0.16 | 59.84 | 49.84
1694 |  |  |  | -0.16 | 59.84 | 49.84
1695 |  |  |  | -0.16 | 59.84 | 49.84
1696 |  |  |  | -0.16 | 59.84 | 49.84
1697 |  |  |  | -0.16 | 59.84 | 49.84
1698 |  |  |  | -0.16 | 59.84 | 49.84
1699 |  |  |  | -0.16 | 59.84 | 49.84
1700 |  |  |  | -0.16 | 59.84 | 49.84
1701 |  |  |  | -0.16 | 59.84 | 49.84
1702 |  |  |  | -0.16 | 59.84 | 49.84
1703 |  |  |  | -0.16 | 59.84 | 49.84
1704 |  |  |  | -0.16 | 59.84 | 49.84
1705 |  |  |  | -0.16 | 59.84 | 49.84
1706 |  |  |  | -0.16 | 59.84 | 49.84
1707 |  |  |  | -0.16 | 59.84 | 49.84
1708 |  |  |  | -0.16 | 59.84 | 49.84
1709 |  |  |  | -0.16 | 59.84 | 49.84
1710 |  |  |  | -0.16 | 59.84 | 49.84
1711 |  |  |  | -0.16 | 59.84 | 49.84
1712 |  |  |  | -0.16 | 59.84 | 49.84
1713 |  |  |  | -0.16 | 59.84 | 49.84
1714 |  |  |  | -0.16 | 59.84 | 49.84
1715 |  |  |  | -0.16 | 59.84 | 49.84
1716 |  |  |  | -0.16 | 59.84 | 49.84
1717 |  |  |  | -0.16 | 59.84 | 49.84
1718 |  |  |  | -0.16 | 59.84 | 49.84
1719 |  |  |  | -0.16 | 59.84 | 49.84
1720 |  |  |  | -0.16 | 59.84 | 49.84
1721 |  |  |  | -0.16 | 59.84 | 49.84
1722 |  |  |  | -0.16 | 59.84 | 49.84
1723 |  |  |  | -0.16 | 59.84 | 49.84
1724 |  |  |  | -0.16 | 59.84 | 49.84
1725 |  |  |  | -0.16 | 59.84 | 49.84
1726 |  |  |  | -0.16 | 59.84 | 49.84
1727 |  |  |  | -0.16 | 59.84 | 49.84
1728 |  |  |  | -0.16 | 59.84 | 49.84
1729 |  |  |  | -0.16 | 59.84 | 49.84
1730 |  |  |  | -0.16 | 59.84 | 49.84
1731 |  |  |  | -0.16 | 59.84 | 49.84
1732 |  |  |  | -0.16 | 59.84 | 49.84
1733 |  |  |  | -0.16 | 59.84 | 49.84
1734 |  |  |  | -0.16 | 59.84 | 49.84
1735 |  |  |  | -0.16 | 59.84 | 49.84
1736 |  |  |  | -0.16 | 59.84 | 49.84
1737 |  |  |  | -0.16 | 59.84 | 49.84
1738 |  |  |  | -0.16 | 59.84 | 49.84
1739 |  |  |  | -0.16 | 59.84 | 49.84
1740 |  |  |  | -0.16 | 59.84 | 49.84
1741 |  |  |  | -0.16 | 59.84 | 49.84
1742 |  |  |  | -0.16 | 59.84 | 49.84
1743 |  |  |  | -0.16 | 59.84 | 49.84
1744 |  |  |  | -0.16 | 59.84 | 49.84
1745 |  |  |  | -0.16 | 59.84 | 49.84
1746 |  |  |  | -0.16 | 59.84 | 49.84
1747 |  |  |  | -0.16 | 59.84 | 49.84
1748 |  |  |  | -0.16 | 59.84 | 49.84
1749 |  |  |  | -0.16 | 59.84 | 49.84
1750 |  |  |  | -0.16 | 59.84 | 49.84
1751 |  |  |  | -0.16 | 59.84 | 49.84
1752 |  |  |  | -0.16 | 59.84 | 49.84
1753 |  |  |  | -0.16 | 59.84 | 49.84
1754 |  |  |  | -0.16 | 59.84 | 49.84
1755 |  |  |  | -0.16 | 59.84 | 49.84
1756 |  |  |  | -0.16 | 59.84 | 49.84
1757 |  |  |  | -0.16 | 59.84 | 49.84
1758 |  |  |  | -0.16 | 59.84 | 49.84
1759 |  |  |  | -0.16 | 59.84 | 49.84
1760 |  |  |  | -0.16 | 59.84 | 49.84
1761 |  |  |  | -0.16 | 59.84 | 49.84
1762 |  |  |  | -0.16 | 59.84 | 49.84
1763 |  |  |  | -0.16 | 59.84 | 49.84
1764 |  |  |  | -0.16 | 59.84 | 49.84
1765 |  |  |  | -0.16 | 59.84 | 49.84
1766 |  |  |  | -0.16 | 59.84 | 49.84
1767 |  |  |  | -0.16 | 59.84 | 49.84
1768 |  |  |  | -0.16 | 59.84 | 49.84
1769 |  |  |  | -0.16 | 59.84 | 49.84
1770 |  |  |  | -0.16 | 59.84 | 49.84
1771 |  |  |  | -0.16 | 59.84 | 49.84
1772 |  |  |  | -0.16 | 59.84 | 49.84
1773 |  |  |  | -0.16 | 59.84 | 49.84
1774 |  |  |  | -0.16 | 59.84 | 49.84
1775 |  |  |  | -0.16 | 59.84 | 49.84
1776 |  |  |  | -0.16 | 59.84 | 49.84
1777 |  |  |  | -0.16 | 59.84 | 49.84
1778 |  |  |  | -0.16 | 59.84 | 49.84
1779 |  |  |  | -0.16 | 59.84 | 49.84
1780 |  |  |  | -0.16 | 59.84 | 49.84
1781 |  |  |  | -0.16 | 59.84 | 49.84
1782 |  |  |  | -0.16 | 59.84 | 49.84
1783 |  |  |  | -0.16 | 59.84 | 49.84
1784 |  |  |  | -0.16 | 59.84 | 49.84
1785 |  |  |  | -0.16 | 59.84 | 49.84
1786 |  |  |  | -0.16 | 59.84 | 49.84
1787 |  |  |  | -0.16 | 59.84 | 49.84
1788 |  |  |  | -0.16 | 59.84 | 49.84
1789 |  |  |  | -0.16 | 59.84 | 49.84
1790 |  |  |  | -0.16 | 59.84 | 49.84
1791 |  |  |  | -0.16 | 59.84 | 49.84
1792 |  |  |  | -0.16 | 59.84 | 49.84
1793 |  |  |  | -0.16 | 59.84 | 49.84
1794 |  |  |  | -0.16 | 59.84 | 49.84
1795 |  |  |  | -0.16 | 59.84 | 49.84
1796 |  |  |  | -0.16 | 59.84 | 49.84
1797 |  |  |  | -0.16 | 59.84 | 49.84
1798 |  |  |  | -0.16 | 59.84 | 49.84
1799 |  |  |  | -0.16 | 59.84 | 49.84
1800 |  |  |  | 0 | 60 | 50
1801 |  |  |  | 0 | 60 | 50
1802 |  |  |  | 0 | 60 | 50
1803 |  |  |  | 0 | 60 | 50
1804 |  |  |  | 0 | 60 | 50
1805 |  |  |  | 0 | 60 | 50
1806 |  |  |  | 0 | 60 | 50
1807 |  |  |  | 0 | 60 | 50
1808 |  |  |  | 0 | 60 | 50
1809 |  |  |  | 0 | 60 | 50
1810 |  |  |  | 0 | 60 | 50
1811 |  |  |  | 0 | 60 | 50
1812 |  |  |  | 0 | 60 | 50
1813 |  |  |  | 0 | 60 | 50
1814 |  |  |  | 0 | 60 | 50
1815 |  |  |  | 0 | 60 | 50
1816 |  |  |  | 0 | 60 | 50
1817 |  |  |  | 0 | 60 | 50
1818 |  |  |  | 0 | 60 | 50
1819 |  |  |  | 0 | 60 | 50
1820 |  |  |  | 0 | 60 | 50
1821 |  |  |  | 0 | 60 | 50
1822 |  |  |  | 0 | 60 | 50
1823 |  |  |  | 0 | 60 | 50
1824 |  |  |  | 0 | 60 | 50
1825 |  |  |  | 0 | 60 | 50
1826 |  |  |  | 0 | 60 | 50
1827 |  |  |  | 0 | 60 | 50
1828 |  |  |  | 0 | 60 | 50
1829 |  |  |  | 0 | 60 | 50
1830 |  |  |  | 0 | 60 | 50
1831 |  |  |  | 0 | 60 | 50
1832 |  |  |  | 0 | 60 | 50
1833 |  |  |  | 0 | 60 | 50
1834 |  |  |  | 0 | 60 | 50
1835 |  |  |  | 0 | 60 | 50
1836 |  |  |  | 0 | 60 | 50
1837 |  |  |  | 0 | 60 | 50
1838 |  |  |  | 0 | 60 | 50
1839 |  |  |  | 0 | 60 | 50
1840 |  |  |  | 0 | 60 | 50
1841 |  |  |  | 0 | 60 | 50
1842 |  |  |  | 0 | 60 | 50
1843 |  |  |  | 0 | 60 | 50
1844 |  |  |  | 0 | 60 | 50
1845 |  |  |  | 0 | 60 | 50
1846 |  |  |  | 0 | 60 | 50
1847 |  |  |  | 0 | 60 | 50
1848 |  |  |  | 0 | 60 | 50
1849 |  |  |  | 0 | 60 | 50
1850 |  |  |  | 0 | 60 | 50
1851 |  |  |  | 0 | 60 | 50
1852 |  |  |  | 0 | 60 | 50
1853 |  |  |  | 0 | 60 | 50
1854 |  |  |  | 0 | 60 | 50
1855 |  |  |  | 0 | 60 | 50
1856 |  |  |  | 0 | 60 | 50
1857 |  |  |  | 0 | 60 | 50
1858 |  |  |  | 0 | 60 | 50
1859 |  |  |  | 0 | 60 | 50

## 3. Test a max charge
Window start |  | 2026-10-15 | 16:30
Baseline [kW]
Enter the date in the first yellow cell and the start time in the second, then the baseline this window runs on in the third. The Date, Time and Baseline columns fill in for every row.
Window 3 of 3: test a from MAXIMUM CHARGE, so the swing spans charge to discharge. Use the column matching your area. 660 s profile plus a 60 s recovery tail.
Elapsed [s] | Date | Time | Baseline [kW] | 50 Hz area offline (−0.200 Hz) | Hokkaido (50 Hz) offline (−0.300 Hz) | 60 Hz area offline (−0.200 Hz)
0 |  |  |  | 50 | 50 | 60
1 |  |  |  | 50 | 50 | 60
2 |  |  |  | 50 | 50 | 60
3 |  |  |  | 50 | 50 | 60
4 |  |  |  | 50 | 50 | 60
5 |  |  |  | 50 | 50 | 60
6 |  |  |  | 50 | 50 | 60
7 |  |  |  | 50 | 50 | 60
8 |  |  |  | 50 | 50 | 60
9 |  |  |  | 50 | 50 | 60
10 |  |  |  | 50 | 50 | 60
11 |  |  |  | 50 | 50 | 60
12 |  |  |  | 50 | 50 | 60
13 |  |  |  | 50 | 50 | 60
14 |  |  |  | 50 | 50 | 60
15 |  |  |  | 50 | 50 | 60
16 |  |  |  | 50 | 50 | 60
17 |  |  |  | 50 | 50 | 60
18 |  |  |  | 50 | 50 | 60
19 |  |  |  | 50 | 50 | 60
20 |  |  |  | 50 | 50 | 60
21 |  |  |  | 50 | 50 | 60
22 |  |  |  | 50 | 50 | 60
23 |  |  |  | 50 | 50 | 60
24 |  |  |  | 50 | 50 | 60
25 |  |  |  | 50 | 50 | 60
26 |  |  |  | 50 | 50 | 60
27 |  |  |  | 50 | 50 | 60
28 |  |  |  | 50 | 50 | 60
29 |  |  |  | 50 | 50 | 60
30 |  |  |  | 50 | 50 | 60
31 |  |  |  | 50 | 50 | 60
32 |  |  |  | 50 | 50 | 60
33 |  |  |  | 50 | 50 | 60
34 |  |  |  | 50 | 50 | 60
35 |  |  |  | 50 | 50 | 60
36 |  |  |  | 50 | 50 | 60
37 |  |  |  | 50 | 50 | 60
38 |  |  |  | 50 | 50 | 60
39 |  |  |  | 50 | 50 | 60
40 |  |  |  | 50 | 50 | 60
41 |  |  |  | 50 | 50 | 60
42 |  |  |  | 50 | 50 | 60
43 |  |  |  | 50 | 50 | 60
44 |  |  |  | 50 | 50 | 60
45 |  |  |  | 50 | 50 | 60
46 |  |  |  | 50 | 50 | 60
47 |  |  |  | 50 | 50 | 60
48 |  |  |  | 50 | 50 | 60
49 |  |  |  | 50 | 50 | 60
50 |  |  |  | 50 | 50 | 60
51 |  |  |  | 50 | 50 | 60
52 |  |  |  | 50 | 50 | 60
53 |  |  |  | 50 | 50 | 60
54 |  |  |  | 50 | 50 | 60
55 |  |  |  | 50 | 50 | 60
56 |  |  |  | 50 | 50 | 60
57 |  |  |  | 50 | 50 | 60
58 |  |  |  | 50 | 50 | 60
59 |  |  |  | 50 | 50 | 60
60 |  |  |  | 49.8 | 49.7 | 59.8
61 |  |  |  | 49.8 | 49.7 | 59.8
62 |  |  |  | 49.8 | 49.7 | 59.8
63 |  |  |  | 49.8 | 49.7 | 59.8
64 |  |  |  | 49.8 | 49.7 | 59.8
65 |  |  |  | 49.8 | 49.7 | 59.8
66 |  |  |  | 49.8 | 49.7 | 59.8
67 |  |  |  | 49.8 | 49.7 | 59.8
68 |  |  |  | 49.8 | 49.7 | 59.8
69 |  |  |  | 49.8 | 49.7 | 59.8
70 |  |  |  | 49.8 | 49.7 | 59.8
71 |  |  |  | 49.8 | 49.7 | 59.8
72 |  |  |  | 49.8 | 49.7 | 59.8
73 |  |  |  | 49.8 | 49.7 | 59.8
74 |  |  |  | 49.8 | 49.7 | 59.8
75 |  |  |  | 49.8 | 49.7 | 59.8
76 |  |  |  | 49.8 | 49.7 | 59.8
77 |  |  |  | 49.8 | 49.7 | 59.8
78 |  |  |  | 49.8 | 49.7 | 59.8
79 |  |  |  | 49.8 | 49.7 | 59.8
80 |  |  |  | 49.8 | 49.7 | 59.8
81 |  |  |  | 49.8 | 49.7 | 59.8
82 |  |  |  | 49.8 | 49.7 | 59.8
83 |  |  |  | 49.8 | 49.7 | 59.8
84 |  |  |  | 49.8 | 49.7 | 59.8
85 |  |  |  | 49.8 | 49.7 | 59.8
86 |  |  |  | 49.8 | 49.7 | 59.8
87 |  |  |  | 49.8 | 49.7 | 59.8
88 |  |  |  | 49.8 | 49.7 | 59.8
89 |  |  |  | 49.8 | 49.7 | 59.8
90 |  |  |  | 49.8 | 49.7 | 59.8
91 |  |  |  | 49.8 | 49.7 | 59.8
92 |  |  |  | 49.8 | 49.7 | 59.8
93 |  |  |  | 49.8 | 49.7 | 59.8
94 |  |  |  | 49.8 | 49.7 | 59.8
95 |  |  |  | 49.8 | 49.7 | 59.8
96 |  |  |  | 49.8 | 49.7 | 59.8
97 |  |  |  | 49.8 | 49.7 | 59.8
98 |  |  |  | 49.8 | 49.7 | 59.8
99 |  |  |  | 49.8 | 49.7 | 59.8
100 |  |  |  | 49.8 | 49.7 | 59.8
101 |  |  |  | 49.8 | 49.7 | 59.8
102 |  |  |  | 49.8 | 49.7 | 59.8
103 |  |  |  | 49.8 | 49.7 | 59.8
104 |  |  |  | 49.8 | 49.7 | 59.8
105 |  |  |  | 49.8 | 49.7 | 59.8
106 |  |  |  | 49.8 | 49.7 | 59.8
107 |  |  |  | 49.8 | 49.7 | 59.8
108 |  |  |  | 49.8 | 49.7 | 59.8
109 |  |  |  | 49.8 | 49.7 | 59.8
110 |  |  |  | 49.8 | 49.7 | 59.8
111 |  |  |  | 49.8 | 49.7 | 59.8
112 |  |  |  | 49.8 | 49.7 | 59.8
113 |  |  |  | 49.8 | 49.7 | 59.8
114 |  |  |  | 49.8 | 49.7 | 59.8
115 |  |  |  | 49.8 | 49.7 | 59.8
116 |  |  |  | 49.8 | 49.7 | 59.8
117 |  |  |  | 49.8 | 49.7 | 59.8
118 |  |  |  | 49.8 | 49.7 | 59.8
119 |  |  |  | 49.8 | 49.7 | 59.8
120 |  |  |  | 49.8 | 49.7 | 59.8
121 |  |  |  | 49.8 | 49.7 | 59.8
122 |  |  |  | 49.8 | 49.7 | 59.8
123 |  |  |  | 49.8 | 49.7 | 59.8
124 |  |  |  | 49.8 | 49.7 | 59.8
125 |  |  |  | 49.8 | 49.7 | 59.8
126 |  |  |  | 49.8 | 49.7 | 59.8
127 |  |  |  | 49.8 | 49.7 | 59.8
128 |  |  |  | 49.8 | 49.7 | 59.8
129 |  |  |  | 49.8 | 49.7 | 59.8
130 |  |  |  | 49.8 | 49.7 | 59.8
131 |  |  |  | 49.8 | 49.7 | 59.8
132 |  |  |  | 49.8 | 49.7 | 59.8
133 |  |  |  | 49.8 | 49.7 | 59.8
134 |  |  |  | 49.8 | 49.7 | 59.8
135 |  |  |  | 49.8 | 49.7 | 59.8
136 |  |  |  | 49.8 | 49.7 | 59.8
137 |  |  |  | 49.8 | 49.7 | 59.8
138 |  |  |  | 49.8 | 49.7 | 59.8
139 |  |  |  | 49.8 | 49.7 | 59.8
140 |  |  |  | 49.8 | 49.7 | 59.8
141 |  |  |  | 49.8 | 49.7 | 59.8
142 |  |  |  | 49.8 | 49.7 | 59.8
143 |  |  |  | 49.8 | 49.7 | 59.8
144 |  |  |  | 49.8 | 49.7 | 59.8
145 |  |  |  | 49.8 | 49.7 | 59.8
146 |  |  |  | 49.8 | 49.7 | 59.8
147 |  |  |  | 49.8 | 49.7 | 59.8
148 |  |  |  | 49.8 | 49.7 | 59.8
149 |  |  |  | 49.8 | 49.7 | 59.8
150 |  |  |  | 49.8 | 49.7 | 59.8
151 |  |  |  | 49.8 | 49.7 | 59.8
152 |  |  |  | 49.8 | 49.7 | 59.8
153 |  |  |  | 49.8 | 49.7 | 59.8
154 |  |  |  | 49.8 | 49.7 | 59.8
155 |  |  |  | 49.8 | 49.7 | 59.8
156 |  |  |  | 49.8 | 49.7 | 59.8
157 |  |  |  | 49.8 | 49.7 | 59.8
158 |  |  |  | 49.8 | 49.7 | 59.8
159 |  |  |  | 49.8 | 49.7 | 59.8
160 |  |  |  | 49.8 | 49.7 | 59.8
161 |  |  |  | 49.8 | 49.7 | 59.8
162 |  |  |  | 49.8 | 49.7 | 59.8
163 |  |  |  | 49.8 | 49.7 | 59.8
164 |  |  |  | 49.8 | 49.7 | 59.8
165 |  |  |  | 49.8 | 49.7 | 59.8
166 |  |  |  | 49.8 | 49.7 | 59.8
167 |  |  |  | 49.8 | 49.7 | 59.8
168 |  |  |  | 49.8 | 49.7 | 59.8
169 |  |  |  | 49.8 | 49.7 | 59.8
170 |  |  |  | 49.8 | 49.7 | 59.8
171 |  |  |  | 49.8 | 49.7 | 59.8
172 |  |  |  | 49.8 | 49.7 | 59.8
173 |  |  |  | 49.8 | 49.7 | 59.8
174 |  |  |  | 49.8 | 49.7 | 59.8
175 |  |  |  | 49.8 | 49.7 | 59.8
176 |  |  |  | 49.8 | 49.7 | 59.8
177 |  |  |  | 49.8 | 49.7 | 59.8
178 |  |  |  | 49.8 | 49.7 | 59.8
179 |  |  |  | 49.8 | 49.7 | 59.8
180 |  |  |  | 49.8 | 49.7 | 59.8
181 |  |  |  | 49.8 | 49.7 | 59.8
182 |  |  |  | 49.8 | 49.7 | 59.8
183 |  |  |  | 49.8 | 49.7 | 59.8
184 |  |  |  | 49.8 | 49.7 | 59.8
185 |  |  |  | 49.8 | 49.7 | 59.8
186 |  |  |  | 49.8 | 49.7 | 59.8
187 |  |  |  | 49.8 | 49.7 | 59.8
188 |  |  |  | 49.8 | 49.7 | 59.8
189 |  |  |  | 49.8 | 49.7 | 59.8
190 |  |  |  | 49.8 | 49.7 | 59.8
191 |  |  |  | 49.8 | 49.7 | 59.8
192 |  |  |  | 49.8 | 49.7 | 59.8
193 |  |  |  | 49.8 | 49.7 | 59.8
194 |  |  |  | 49.8 | 49.7 | 59.8
195 |  |  |  | 49.8 | 49.7 | 59.8
196 |  |  |  | 49.8 | 49.7 | 59.8
197 |  |  |  | 49.8 | 49.7 | 59.8
198 |  |  |  | 49.8 | 49.7 | 59.8
199 |  |  |  | 49.8 | 49.7 | 59.8
200 |  |  |  | 49.8 | 49.7 | 59.8
201 |  |  |  | 49.8 | 49.7 | 59.8
202 |  |  |  | 49.8 | 49.7 | 59.8
203 |  |  |  | 49.8 | 49.7 | 59.8
204 |  |  |  | 49.8 | 49.7 | 59.8
205 |  |  |  | 49.8 | 49.7 | 59.8
206 |  |  |  | 49.8 | 49.7 | 59.8
207 |  |  |  | 49.8 | 49.7 | 59.8
208 |  |  |  | 49.8 | 49.7 | 59.8
209 |  |  |  | 49.8 | 49.7 | 59.8
210 |  |  |  | 49.8 | 49.7 | 59.8
211 |  |  |  | 49.8 | 49.7 | 59.8
212 |  |  |  | 49.8 | 49.7 | 59.8
213 |  |  |  | 49.8 | 49.7 | 59.8
214 |  |  |  | 49.8 | 49.7 | 59.8
215 |  |  |  | 49.8 | 49.7 | 59.8
216 |  |  |  | 49.8 | 49.7 | 59.8
217 |  |  |  | 49.8 | 49.7 | 59.8
218 |  |  |  | 49.8 | 49.7 | 59.8
219 |  |  |  | 49.8 | 49.7 | 59.8
220 |  |  |  | 49.8 | 49.7 | 59.8
221 |  |  |  | 49.8 | 49.7 | 59.8
222 |  |  |  | 49.8 | 49.7 | 59.8
223 |  |  |  | 49.8 | 49.7 | 59.8
224 |  |  |  | 49.8 | 49.7 | 59.8
225 |  |  |  | 49.8 | 49.7 | 59.8
226 |  |  |  | 49.8 | 49.7 | 59.8
227 |  |  |  | 49.8 | 49.7 | 59.8
228 |  |  |  | 49.8 | 49.7 | 59.8
229 |  |  |  | 49.8 | 49.7 | 59.8
230 |  |  |  | 49.8 | 49.7 | 59.8
231 |  |  |  | 49.8 | 49.7 | 59.8
232 |  |  |  | 49.8 | 49.7 | 59.8
233 |  |  |  | 49.8 | 49.7 | 59.8
234 |  |  |  | 49.8 | 49.7 | 59.8
235 |  |  |  | 49.8 | 49.7 | 59.8
236 |  |  |  | 49.8 | 49.7 | 59.8
237 |  |  |  | 49.8 | 49.7 | 59.8
238 |  |  |  | 49.8 | 49.7 | 59.8
239 |  |  |  | 49.8 | 49.7 | 59.8
240 |  |  |  | 49.8 | 49.7 | 59.8
241 |  |  |  | 49.8 | 49.7 | 59.8
242 |  |  |  | 49.8 | 49.7 | 59.8
243 |  |  |  | 49.8 | 49.7 | 59.8
244 |  |  |  | 49.8 | 49.7 | 59.8
245 |  |  |  | 49.8 | 49.7 | 59.8
246 |  |  |  | 49.8 | 49.7 | 59.8
247 |  |  |  | 49.8 | 49.7 | 59.8
248 |  |  |  | 49.8 | 49.7 | 59.8
249 |  |  |  | 49.8 | 49.7 | 59.8
250 |  |  |  | 49.8 | 49.7 | 59.8
251 |  |  |  | 49.8 | 49.7 | 59.8
252 |  |  |  | 49.8 | 49.7 | 59.8
253 |  |  |  | 49.8 | 49.7 | 59.8
254 |  |  |  | 49.8 | 49.7 | 59.8
255 |  |  |  | 49.8 | 49.7 | 59.8
256 |  |  |  | 49.8 | 49.7 | 59.8
257 |  |  |  | 49.8 | 49.7 | 59.8
258 |  |  |  | 49.8 | 49.7 | 59.8
259 |  |  |  | 49.8 | 49.7 | 59.8
260 |  |  |  | 49.8 | 49.7 | 59.8
261 |  |  |  | 49.8 | 49.7 | 59.8
262 |  |  |  | 49.8 | 49.7 | 59.8
263 |  |  |  | 49.8 | 49.7 | 59.8
264 |  |  |  | 49.8 | 49.7 | 59.8
265 |  |  |  | 49.8 | 49.7 | 59.8
266 |  |  |  | 49.8 | 49.7 | 59.8
267 |  |  |  | 49.8 | 49.7 | 59.8
268 |  |  |  | 49.8 | 49.7 | 59.8
269 |  |  |  | 49.8 | 49.7 | 59.8
270 |  |  |  | 49.8 | 49.7 | 59.8
271 |  |  |  | 49.8 | 49.7 | 59.8
272 |  |  |  | 49.8 | 49.7 | 59.8
273 |  |  |  | 49.8 | 49.7 | 59.8
274 |  |  |  | 49.8 | 49.7 | 59.8
275 |  |  |  | 49.8 | 49.7 | 59.8
276 |  |  |  | 49.8 | 49.7 | 59.8
277 |  |  |  | 49.8 | 49.7 | 59.8
278 |  |  |  | 49.8 | 49.7 | 59.8
279 |  |  |  | 49.8 | 49.7 | 59.8
280 |  |  |  | 49.8 | 49.7 | 59.8
281 |  |  |  | 49.8 | 49.7 | 59.8
282 |  |  |  | 49.8 | 49.7 | 59.8
283 |  |  |  | 49.8 | 49.7 | 59.8
284 |  |  |  | 49.8 | 49.7 | 59.8
285 |  |  |  | 49.8 | 49.7 | 59.8
286 |  |  |  | 49.8 | 49.7 | 59.8
287 |  |  |  | 49.8 | 49.7 | 59.8
288 |  |  |  | 49.8 | 49.7 | 59.8
289 |  |  |  | 49.8 | 49.7 | 59.8
290 |  |  |  | 49.8 | 49.7 | 59.8
291 |  |  |  | 49.8 | 49.7 | 59.8
292 |  |  |  | 49.8 | 49.7 | 59.8
293 |  |  |  | 49.8 | 49.7 | 59.8
294 |  |  |  | 49.8 | 49.7 | 59.8
295 |  |  |  | 49.8 | 49.7 | 59.8
296 |  |  |  | 49.8 | 49.7 | 59.8
297 |  |  |  | 49.8 | 49.7 | 59.8
298 |  |  |  | 49.8 | 49.7 | 59.8
299 |  |  |  | 49.8 | 49.7 | 59.8
300 |  |  |  | 49.8 | 49.7 | 59.8
301 |  |  |  | 49.8 | 49.7 | 59.8
302 |  |  |  | 49.8 | 49.7 | 59.8
303 |  |  |  | 49.8 | 49.7 | 59.8
304 |  |  |  | 49.8 | 49.7 | 59.8
305 |  |  |  | 49.8 | 49.7 | 59.8
306 |  |  |  | 49.8 | 49.7 | 59.8
307 |  |  |  | 49.8 | 49.7 | 59.8
308 |  |  |  | 49.8 | 49.7 | 59.8
309 |  |  |  | 49.8 | 49.7 | 59.8
310 |  |  |  | 49.8 | 49.7 | 59.8
311 |  |  |  | 49.8 | 49.7 | 59.8
312 |  |  |  | 49.8 | 49.7 | 59.8
313 |  |  |  | 49.8 | 49.7 | 59.8
314 |  |  |  | 49.8 | 49.7 | 59.8
315 |  |  |  | 49.8 | 49.7 | 59.8
316 |  |  |  | 49.8 | 49.7 | 59.8
317 |  |  |  | 49.8 | 49.7 | 59.8
318 |  |  |  | 49.8 | 49.7 | 59.8
319 |  |  |  | 49.8 | 49.7 | 59.8
320 |  |  |  | 49.8 | 49.7 | 59.8
321 |  |  |  | 49.8 | 49.7 | 59.8
322 |  |  |  | 49.8 | 49.7 | 59.8
323 |  |  |  | 49.8 | 49.7 | 59.8
324 |  |  |  | 49.8 | 49.7 | 59.8
325 |  |  |  | 49.8 | 49.7 | 59.8
326 |  |  |  | 49.8 | 49.7 | 59.8
327 |  |  |  | 49.8 | 49.7 | 59.8
328 |  |  |  | 49.8 | 49.7 | 59.8
329 |  |  |  | 49.8 | 49.7 | 59.8
330 |  |  |  | 49.8 | 49.7 | 59.8
331 |  |  |  | 49.8 | 49.7 | 59.8
332 |  |  |  | 49.8 | 49.7 | 59.8
333 |  |  |  | 49.8 | 49.7 | 59.8
334 |  |  |  | 49.8 | 49.7 | 59.8
335 |  |  |  | 49.8 | 49.7 | 59.8
336 |  |  |  | 49.8 | 49.7 | 59.8
337 |  |  |  | 49.8 | 49.7 | 59.8
338 |  |  |  | 49.8 | 49.7 | 59.8
339 |  |  |  | 49.8 | 49.7 | 59.8
340 |  |  |  | 49.8 | 49.7 | 59.8
341 |  |  |  | 49.8 | 49.7 | 59.8
342 |  |  |  | 49.8 | 49.7 | 59.8
343 |  |  |  | 49.8 | 49.7 | 59.8
344 |  |  |  | 49.8 | 49.7 | 59.8
345 |  |  |  | 49.8 | 49.7 | 59.8
346 |  |  |  | 49.8 | 49.7 | 59.8
347 |  |  |  | 49.8 | 49.7 | 59.8
348 |  |  |  | 49.8 | 49.7 | 59.8
349 |  |  |  | 49.8 | 49.7 | 59.8
350 |  |  |  | 49.8 | 49.7 | 59.8
351 |  |  |  | 49.8 | 49.7 | 59.8
352 |  |  |  | 49.8 | 49.7 | 59.8
353 |  |  |  | 49.8 | 49.7 | 59.8
354 |  |  |  | 49.8 | 49.7 | 59.8
355 |  |  |  | 49.8 | 49.7 | 59.8
356 |  |  |  | 49.8 | 49.7 | 59.8
357 |  |  |  | 49.8 | 49.7 | 59.8
358 |  |  |  | 49.8 | 49.7 | 59.8
359 |  |  |  | 49.8 | 49.7 | 59.8
360 |  |  |  | 49.8 | 49.7 | 59.8
361 |  |  |  | 49.8 | 49.7 | 59.8
362 |  |  |  | 49.8 | 49.7 | 59.8
363 |  |  |  | 49.8 | 49.7 | 59.8
364 |  |  |  | 49.8 | 49.7 | 59.8
365 |  |  |  | 49.8 | 49.7 | 59.8
366 |  |  |  | 49.8 | 49.7 | 59.8
367 |  |  |  | 49.8 | 49.7 | 59.8
368 |  |  |  | 49.8 | 49.7 | 59.8
369 |  |  |  | 49.8 | 49.7 | 59.8
370 |  |  |  | 49.8 | 49.7 | 59.8
371 |  |  |  | 49.8 | 49.7 | 59.8
372 |  |  |  | 49.8 | 49.7 | 59.8
373 |  |  |  | 49.8 | 49.7 | 59.8
374 |  |  |  | 49.8 | 49.7 | 59.8
375 |  |  |  | 49.8 | 49.7 | 59.8
376 |  |  |  | 49.8 | 49.7 | 59.8
377 |  |  |  | 49.8 | 49.7 | 59.8
378 |  |  |  | 49.8 | 49.7 | 59.8
379 |  |  |  | 49.8 | 49.7 | 59.8
380 |  |  |  | 49.8 | 49.7 | 59.8
381 |  |  |  | 49.8 | 49.7 | 59.8
382 |  |  |  | 49.8 | 49.7 | 59.8
383 |  |  |  | 49.8 | 49.7 | 59.8
384 |  |  |  | 49.8 | 49.7 | 59.8
385 |  |  |  | 49.8 | 49.7 | 59.8
386 |  |  |  | 49.8 | 49.7 | 59.8
387 |  |  |  | 49.8 | 49.7 | 59.8
388 |  |  |  | 49.8 | 49.7 | 59.8
389 |  |  |  | 49.8 | 49.7 | 59.8
390 |  |  |  | 49.8 | 49.7 | 59.8
391 |  |  |  | 49.8 | 49.7 | 59.8
392 |  |  |  | 49.8 | 49.7 | 59.8
393 |  |  |  | 49.8 | 49.7 | 59.8
394 |  |  |  | 49.8 | 49.7 | 59.8
395 |  |  |  | 49.8 | 49.7 | 59.8
396 |  |  |  | 49.8 | 49.7 | 59.8
397 |  |  |  | 49.8 | 49.7 | 59.8
398 |  |  |  | 49.8 | 49.7 | 59.8
399 |  |  |  | 49.8 | 49.7 | 59.8
400 |  |  |  | 49.8 | 49.7 | 59.8
401 |  |  |  | 49.8 | 49.7 | 59.8
402 |  |  |  | 49.8 | 49.7 | 59.8
403 |  |  |  | 49.8 | 49.7 | 59.8
404 |  |  |  | 49.8 | 49.7 | 59.8
405 |  |  |  | 49.8 | 49.7 | 59.8
406 |  |  |  | 49.8 | 49.7 | 59.8
407 |  |  |  | 49.8 | 49.7 | 59.8
408 |  |  |  | 49.8 | 49.7 | 59.8
409 |  |  |  | 49.8 | 49.7 | 59.8
410 |  |  |  | 49.8 | 49.7 | 59.8
411 |  |  |  | 49.8 | 49.7 | 59.8
412 |  |  |  | 49.8 | 49.7 | 59.8
413 |  |  |  | 49.8 | 49.7 | 59.8
414 |  |  |  | 49.8 | 49.7 | 59.8
415 |  |  |  | 49.8 | 49.7 | 59.8
416 |  |  |  | 49.8 | 49.7 | 59.8
417 |  |  |  | 49.8 | 49.7 | 59.8
418 |  |  |  | 49.8 | 49.7 | 59.8
419 |  |  |  | 49.8 | 49.7 | 59.8
420 |  |  |  | 49.8 | 49.7 | 59.8
421 |  |  |  | 49.8 | 49.7 | 59.8
422 |  |  |  | 49.8 | 49.7 | 59.8
423 |  |  |  | 49.8 | 49.7 | 59.8
424 |  |  |  | 49.8 | 49.7 | 59.8
425 |  |  |  | 49.8 | 49.7 | 59.8
426 |  |  |  | 49.8 | 49.7 | 59.8
427 |  |  |  | 49.8 | 49.7 | 59.8
428 |  |  |  | 49.8 | 49.7 | 59.8
429 |  |  |  | 49.8 | 49.7 | 59.8
430 |  |  |  | 49.8 | 49.7 | 59.8
431 |  |  |  | 49.8 | 49.7 | 59.8
432 |  |  |  | 49.8 | 49.7 | 59.8
433 |  |  |  | 49.8 | 49.7 | 59.8
434 |  |  |  | 49.8 | 49.7 | 59.8
435 |  |  |  | 49.8 | 49.7 | 59.8
436 |  |  |  | 49.8 | 49.7 | 59.8
437 |  |  |  | 49.8 | 49.7 | 59.8
438 |  |  |  | 49.8 | 49.7 | 59.8
439 |  |  |  | 49.8 | 49.7 | 59.8
440 |  |  |  | 49.8 | 49.7 | 59.8
441 |  |  |  | 49.8 | 49.7 | 59.8
442 |  |  |  | 49.8 | 49.7 | 59.8
443 |  |  |  | 49.8 | 49.7 | 59.8
444 |  |  |  | 49.8 | 49.7 | 59.8
445 |  |  |  | 49.8 | 49.7 | 59.8
446 |  |  |  | 49.8 | 49.7 | 59.8
447 |  |  |  | 49.8 | 49.7 | 59.8
448 |  |  |  | 49.8 | 49.7 | 59.8
449 |  |  |  | 49.8 | 49.7 | 59.8
450 |  |  |  | 49.8 | 49.7 | 59.8
451 |  |  |  | 49.8 | 49.7 | 59.8
452 |  |  |  | 49.8 | 49.7 | 59.8
453 |  |  |  | 49.8 | 49.7 | 59.8
454 |  |  |  | 49.8 | 49.7 | 59.8
455 |  |  |  | 49.8 | 49.7 | 59.8
456 |  |  |  | 49.8 | 49.7 | 59.8
457 |  |  |  | 49.8 | 49.7 | 59.8
458 |  |  |  | 49.8 | 49.7 | 59.8
459 |  |  |  | 49.8 | 49.7 | 59.8
460 |  |  |  | 49.8 | 49.7 | 59.8
461 |  |  |  | 49.8 | 49.7 | 59.8
462 |  |  |  | 49.8 | 49.7 | 59.8
463 |  |  |  | 49.8 | 49.7 | 59.8
464 |  |  |  | 49.8 | 49.7 | 59.8
465 |  |  |  | 49.8 | 49.7 | 59.8
466 |  |  |  | 49.8 | 49.7 | 59.8
467 |  |  |  | 49.8 | 49.7 | 59.8
468 |  |  |  | 49.8 | 49.7 | 59.8
469 |  |  |  | 49.8 | 49.7 | 59.8
470 |  |  |  | 49.8 | 49.7 | 59.8
471 |  |  |  | 49.8 | 49.7 | 59.8
472 |  |  |  | 49.8 | 49.7 | 59.8
473 |  |  |  | 49.8 | 49.7 | 59.8
474 |  |  |  | 49.8 | 49.7 | 59.8
475 |  |  |  | 49.8 | 49.7 | 59.8
476 |  |  |  | 49.8 | 49.7 | 59.8
477 |  |  |  | 49.8 | 49.7 | 59.8
478 |  |  |  | 49.8 | 49.7 | 59.8
479 |  |  |  | 49.8 | 49.7 | 59.8
480 |  |  |  | 49.8 | 49.7 | 59.8
481 |  |  |  | 49.8 | 49.7 | 59.8
482 |  |  |  | 49.8 | 49.7 | 59.8
483 |  |  |  | 49.8 | 49.7 | 59.8
484 |  |  |  | 49.8 | 49.7 | 59.8
485 |  |  |  | 49.8 | 49.7 | 59.8
486 |  |  |  | 49.8 | 49.7 | 59.8
487 |  |  |  | 49.8 | 49.7 | 59.8
488 |  |  |  | 49.8 | 49.7 | 59.8
489 |  |  |  | 49.8 | 49.7 | 59.8
490 |  |  |  | 49.8 | 49.7 | 59.8
491 |  |  |  | 49.8 | 49.7 | 59.8
492 |  |  |  | 49.8 | 49.7 | 59.8
493 |  |  |  | 49.8 | 49.7 | 59.8
494 |  |  |  | 49.8 | 49.7 | 59.8
495 |  |  |  | 49.8 | 49.7 | 59.8
496 |  |  |  | 49.8 | 49.7 | 59.8
497 |  |  |  | 49.8 | 49.7 | 59.8
498 |  |  |  | 49.8 | 49.7 | 59.8
499 |  |  |  | 49.8 | 49.7 | 59.8
500 |  |  |  | 49.8 | 49.7 | 59.8
501 |  |  |  | 49.8 | 49.7 | 59.8
502 |  |  |  | 49.8 | 49.7 | 59.8
503 |  |  |  | 49.8 | 49.7 | 59.8
504 |  |  |  | 49.8 | 49.7 | 59.8
505 |  |  |  | 49.8 | 49.7 | 59.8
506 |  |  |  | 49.8 | 49.7 | 59.8
507 |  |  |  | 49.8 | 49.7 | 59.8
508 |  |  |  | 49.8 | 49.7 | 59.8
509 |  |  |  | 49.8 | 49.7 | 59.8
510 |  |  |  | 49.8 | 49.7 | 59.8
511 |  |  |  | 49.8 | 49.7 | 59.8
512 |  |  |  | 49.8 | 49.7 | 59.8
513 |  |  |  | 49.8 | 49.7 | 59.8
514 |  |  |  | 49.8 | 49.7 | 59.8
515 |  |  |  | 49.8 | 49.7 | 59.8
516 |  |  |  | 49.8 | 49.7 | 59.8
517 |  |  |  | 49.8 | 49.7 | 59.8
518 |  |  |  | 49.8 | 49.7 | 59.8
519 |  |  |  | 49.8 | 49.7 | 59.8
520 |  |  |  | 49.8 | 49.7 | 59.8
521 |  |  |  | 49.8 | 49.7 | 59.8
522 |  |  |  | 49.8 | 49.7 | 59.8
523 |  |  |  | 49.8 | 49.7 | 59.8
524 |  |  |  | 49.8 | 49.7 | 59.8
525 |  |  |  | 49.8 | 49.7 | 59.8
526 |  |  |  | 49.8 | 49.7 | 59.8
527 |  |  |  | 49.8 | 49.7 | 59.8
528 |  |  |  | 49.8 | 49.7 | 59.8
529 |  |  |  | 49.8 | 49.7 | 59.8
530 |  |  |  | 49.8 | 49.7 | 59.8
531 |  |  |  | 49.8 | 49.7 | 59.8
532 |  |  |  | 49.8 | 49.7 | 59.8
533 |  |  |  | 49.8 | 49.7 | 59.8
534 |  |  |  | 49.8 | 49.7 | 59.8
535 |  |  |  | 49.8 | 49.7 | 59.8
536 |  |  |  | 49.8 | 49.7 | 59.8
537 |  |  |  | 49.8 | 49.7 | 59.8
538 |  |  |  | 49.8 | 49.7 | 59.8
539 |  |  |  | 49.8 | 49.7 | 59.8
540 |  |  |  | 49.8 | 49.7 | 59.8
541 |  |  |  | 49.8 | 49.7 | 59.8
542 |  |  |  | 49.8 | 49.7 | 59.8
543 |  |  |  | 49.8 | 49.7 | 59.8
544 |  |  |  | 49.8 | 49.7 | 59.8
545 |  |  |  | 49.8 | 49.7 | 59.8
546 |  |  |  | 49.8 | 49.7 | 59.8
547 |  |  |  | 49.8 | 49.7 | 59.8
548 |  |  |  | 49.8 | 49.7 | 59.8
549 |  |  |  | 49.8 | 49.7 | 59.8
550 |  |  |  | 49.8 | 49.7 | 59.8
551 |  |  |  | 49.8 | 49.7 | 59.8
552 |  |  |  | 49.8 | 49.7 | 59.8
553 |  |  |  | 49.8 | 49.7 | 59.8
554 |  |  |  | 49.8 | 49.7 | 59.8
555 |  |  |  | 49.8 | 49.7 | 59.8
556 |  |  |  | 49.8 | 49.7 | 59.8
557 |  |  |  | 49.8 | 49.7 | 59.8
558 |  |  |  | 49.8 | 49.7 | 59.8
559 |  |  |  | 49.8 | 49.7 | 59.8
560 |  |  |  | 49.8 | 49.7 | 59.8
561 |  |  |  | 49.8 | 49.7 | 59.8
562 |  |  |  | 49.8 | 49.7 | 59.8
563 |  |  |  | 49.8 | 49.7 | 59.8
564 |  |  |  | 49.8 | 49.7 | 59.8
565 |  |  |  | 49.8 | 49.7 | 59.8
566 |  |  |  | 49.8 | 49.7 | 59.8
567 |  |  |  | 49.8 | 49.7 | 59.8
568 |  |  |  | 49.8 | 49.7 | 59.8
569 |  |  |  | 49.8 | 49.7 | 59.8
570 |  |  |  | 49.8 | 49.7 | 59.8
571 |  |  |  | 49.8 | 49.7 | 59.8
572 |  |  |  | 49.8 | 49.7 | 59.8
573 |  |  |  | 49.8 | 49.7 | 59.8
574 |  |  |  | 49.8 | 49.7 | 59.8
575 |  |  |  | 49.8 | 49.7 | 59.8
576 |  |  |  | 49.8 | 49.7 | 59.8
577 |  |  |  | 49.8 | 49.7 | 59.8
578 |  |  |  | 49.8 | 49.7 | 59.8
579 |  |  |  | 49.8 | 49.7 | 59.8
580 |  |  |  | 49.8 | 49.7 | 59.8
581 |  |  |  | 49.8 | 49.7 | 59.8
582 |  |  |  | 49.8 | 49.7 | 59.8
583 |  |  |  | 49.8 | 49.7 | 59.8
584 |  |  |  | 49.8 | 49.7 | 59.8
585 |  |  |  | 49.8 | 49.7 | 59.8
586 |  |  |  | 49.8 | 49.7 | 59.8
587 |  |  |  | 49.8 | 49.7 | 59.8
588 |  |  |  | 49.8 | 49.7 | 59.8
589 |  |  |  | 49.8 | 49.7 | 59.8
590 |  |  |  | 49.8 | 49.7 | 59.8
591 |  |  |  | 49.8 | 49.7 | 59.8
592 |  |  |  | 49.8 | 49.7 | 59.8
593 |  |  |  | 49.8 | 49.7 | 59.8
594 |  |  |  | 49.8 | 49.7 | 59.8
595 |  |  |  | 49.8 | 49.7 | 59.8
596 |  |  |  | 49.8 | 49.7 | 59.8
597 |  |  |  | 49.8 | 49.7 | 59.8
598 |  |  |  | 49.8 | 49.7 | 59.8
599 |  |  |  | 49.8 | 49.7 | 59.8
600 |  |  |  | 49.8 | 49.7 | 59.8
601 |  |  |  | 49.8 | 49.7 | 59.8
602 |  |  |  | 49.8 | 49.7 | 59.8
603 |  |  |  | 49.8 | 49.7 | 59.8
604 |  |  |  | 49.8 | 49.7 | 59.8
605 |  |  |  | 49.8 | 49.7 | 59.8
606 |  |  |  | 49.8 | 49.7 | 59.8
607 |  |  |  | 49.8 | 49.7 | 59.8
608 |  |  |  | 49.8 | 49.7 | 59.8
609 |  |  |  | 49.8 | 49.7 | 59.8
610 |  |  |  | 49.8 | 49.7 | 59.8
611 |  |  |  | 49.8 | 49.7 | 59.8
612 |  |  |  | 49.8 | 49.7 | 59.8
613 |  |  |  | 49.8 | 49.7 | 59.8
614 |  |  |  | 49.8 | 49.7 | 59.8
615 |  |  |  | 49.8 | 49.7 | 59.8
616 |  |  |  | 49.8 | 49.7 | 59.8
617 |  |  |  | 49.8 | 49.7 | 59.8
618 |  |  |  | 49.8 | 49.7 | 59.8
619 |  |  |  | 49.8 | 49.7 | 59.8
620 |  |  |  | 49.8 | 49.7 | 59.8
621 |  |  |  | 49.8 | 49.7 | 59.8
622 |  |  |  | 49.8 | 49.7 | 59.8
623 |  |  |  | 49.8 | 49.7 | 59.8
624 |  |  |  | 49.8 | 49.7 | 59.8
625 |  |  |  | 49.8 | 49.7 | 59.8
626 |  |  |  | 49.8 | 49.7 | 59.8
627 |  |  |  | 49.8 | 49.7 | 59.8
628 |  |  |  | 49.8 | 49.7 | 59.8
629 |  |  |  | 49.8 | 49.7 | 59.8
630 |  |  |  | 49.8 | 49.7 | 59.8
631 |  |  |  | 49.8 | 49.7 | 59.8
632 |  |  |  | 49.8 | 49.7 | 59.8
633 |  |  |  | 49.8 | 49.7 | 59.8
634 |  |  |  | 49.8 | 49.7 | 59.8
635 |  |  |  | 49.8 | 49.7 | 59.8
636 |  |  |  | 49.8 | 49.7 | 59.8
637 |  |  |  | 49.8 | 49.7 | 59.8
638 |  |  |  | 49.8 | 49.7 | 59.8
639 |  |  |  | 49.8 | 49.7 | 59.8
640 |  |  |  | 49.8 | 49.7 | 59.8
641 |  |  |  | 49.8 | 49.7 | 59.8
642 |  |  |  | 49.8 | 49.7 | 59.8
643 |  |  |  | 49.8 | 49.7 | 59.8
644 |  |  |  | 49.8 | 49.7 | 59.8
645 |  |  |  | 49.8 | 49.7 | 59.8
646 |  |  |  | 49.8 | 49.7 | 59.8
647 |  |  |  | 49.8 | 49.7 | 59.8
648 |  |  |  | 49.8 | 49.7 | 59.8
649 |  |  |  | 49.8 | 49.7 | 59.8
650 |  |  |  | 49.8 | 49.7 | 59.8
651 |  |  |  | 49.8 | 49.7 | 59.8
652 |  |  |  | 49.8 | 49.7 | 59.8
653 |  |  |  | 49.8 | 49.7 | 59.8
654 |  |  |  | 49.8 | 49.7 | 59.8
655 |  |  |  | 49.8 | 49.7 | 59.8
656 |  |  |  | 49.8 | 49.7 | 59.8
657 |  |  |  | 49.8 | 49.7 | 59.8
658 |  |  |  | 49.8 | 49.7 | 59.8
659 |  |  |  | 49.8 | 49.7 | 59.8
660 |  |  |  | 50 | 50 | 60
661 |  |  |  | 50 | 50 | 60
662 |  |  |  | 50 | 50 | 60
663 |  |  |  | 50 | 50 | 60
664 |  |  |  | 50 | 50 | 60
665 |  |  |  | 50 | 50 | 60
666 |  |  |  | 50 | 50 | 60
667 |  |  |  | 50 | 50 | 60
668 |  |  |  | 50 | 50 | 60
669 |  |  |  | 50 | 50 | 60
670 |  |  |  | 50 | 50 | 60
671 |  |  |  | 50 | 50 | 60
672 |  |  |  | 50 | 50 | 60
673 |  |  |  | 50 | 50 | 60
674 |  |  |  | 50 | 50 | 60
675 |  |  |  | 50 | 50 | 60
676 |  |  |  | 50 | 50 | 60
677 |  |  |  | 50 | 50 | 60
678 |  |  |  | 50 | 50 | 60
679 |  |  |  | 50 | 50 | 60
680 |  |  |  | 50 | 50 | 60
681 |  |  |  | 50 | 50 | 60
682 |  |  |  | 50 | 50 | 60
683 |  |  |  | 50 | 50 | 60
684 |  |  |  | 50 | 50 | 60
685 |  |  |  | 50 | 50 | 60
686 |  |  |  | 50 | 50 | 60
687 |  |  |  | 50 | 50 | 60
688 |  |  |  | 50 | 50 | 60
689 |  |  |  | 50 | 50 | 60
690 |  |  |  | 50 | 50 | 60
691 |  |  |  | 50 | 50 | 60
692 |  |  |  | 50 | 50 | 60
693 |  |  |  | 50 | 50 | 60
694 |  |  |  | 50 | 50 | 60
695 |  |  |  | 50 | 50 | 60
696 |  |  |  | 50 | 50 | 60
697 |  |  |  | 50 | 50 | 60
698 |  |  |  | 50 | 50 | 60
699 |  |  |  | 50 | 50 | 60
700 |  |  |  | 50 | 50 | 60
701 |  |  |  | 50 | 50 | 60
702 |  |  |  | 50 | 50 | 60
703 |  |  |  | 50 | 50 | 60
704 |  |  |  | 50 | 50 | 60
705 |  |  |  | 50 | 50 | 60
706 |  |  |  | 50 | 50 | 60
707 |  |  |  | 50 | 50 | 60
708 |  |  |  | 50 | 50 | 60
709 |  |  |  | 50 | 50 | 60
710 |  |  |  | 50 | 50 | 60
711 |  |  |  | 50 | 50 | 60
712 |  |  |  | 50 | 50 | 60
713 |  |  |  | 50 | 50 | 60
714 |  |  |  | 50 | 50 | 60
715 |  |  |  | 50 | 50 | 60
716 |  |  |  | 50 | 50 | 60
717 |  |  |  | 50 | 50 | 60
718 |  |  |  | 50 | 50 | 60
719 |  |  |  | 50 | 50 | 60

## Pattern tables
Pattern tables
These tables are the two injection profiles reduced to their transition points. Test b is used for windows 1 and 2, test a for window 3; what separates windows 1 and 2 is the baseline, not the frequency.
Use them before the run to confirm what is loaded into the transducer: the number of levels, the magnitude of each step, and how long each level is held. Every row is one transition; the Hold column is how long that level lasts before the next row takes over.
Test b (normal conditions): 1,800 s
Time [s] | Hold [s] | Deviation [Hz] | Frequency [Hz] 60 Hz area | Frequency [Hz] 50 Hz area
0 | 30 | 0 | 60 | 50
30 | 120 | 0.01 | 60.01 | 50.01
150 | 30 | 0 | 60 | 50
180 | 120 | -0.01 | 59.99 | 49.99
300 | 30 | 0 | 60 | 50
330 | 120 | 0.03 | 60.03 | 50.03
450 | 30 | 0 | 60 | 50
480 | 120 | -0.03 | 59.97 | 49.97
600 | 30 | 0 | 60 | 50
630 | 120 | 0.05 | 60.05 | 50.05
750 | 30 | 0 | 60 | 50
780 | 120 | -0.05 | 59.95 | 49.95
900 | 30 | 0 | 60 | 50
930 | 120 | 0.08 | 60.08 | 50.08
1050 | 30 | 0 | 60 | 50
1080 | 120 | -0.08 | 59.92 | 49.92
1200 | 30 | 0 | 60 | 50
1230 | 120 | 0.12 | 60.12 | 50.12
1350 | 30 | 0 | 60 | 50
1380 | 120 | -0.12 | 59.88 | 49.88
1500 | 30 | 0 | 60 | 50
1530 | 120 | 0.16 | 60.16 | 50.16
1650 | 30 | 0 | 60 | 50
1680 | 120 | -0.16 | 59.84 | 49.84
1800 | 60 | 0 | 60 | 50
Test a (abnormal conditions): 660 s
Time [s] | Deviation | Hold [s] | 50 Hz area offline (−0.200 Hz) | Hokkaido (50 Hz) offline (−0.300 Hz) | 60 Hz area offline (−0.200 Hz)
0 | 0 | 60 | 50 | 50 | 60
60 | step down | 600 | 49.8 | 49.7 | 59.8
660 | 0 | 60 | 50 | 50 | 60