## Integrator checklist
Tensor Cloud battery optimization - Integrator checklist (protocol 2.6.0)
Fill in the Result column with PASS, FAIL, N/A, or leave blank for not-yet-run. Use Notes for follow-ups. Online reference: https://docs.tensorenergy.jp/api/battery-optimization/integrator-checklist
Module | Test ID | Test name | Description | Pass criteria | Applies to | Result | Notes
Connection | C-1 | TLS to broker endpoint | Open a TLS connection to the documented broker hostname on port 8883. Validate the server certificate against the Tensor Cloud CA chain. | Connection established, server certificate verified, plaintext on :1883 refused. | All
Connection | C-2 | Per-gateway certificate uniqueness | Confirm each gateway is provisioned with its own client certificate. Attempt a second concurrent connection using the same certificate from a different host. AWS IoT Core disconnects the older session. | Each gateway has a unique certificate; opening a second concurrent connection with the same certificate disconnects the first. | All
Connection | C-3 | CA chain validation | EMS validates the broker certificate against the documented CA chain. Reject connections when the chain is broken or expired. | Invalid or self-signed broker certificate is rejected. | All
Connection | C-7 | QoS and application-level acknowledgement | The EMS uses MQTT QoS 0 or 1 as appropriate; both are supported by the broker. Regardless of QoS, the EMS sends an application-level CommandResponse on ack-cmd/{siteId} for every command received, since it carries validation results, not delivery confirmation. | EMS publishes at QoS 0 or 1; EMS sends an application-level CommandResponse for every command received, independent of the MQTT QoS in use. | All
Connection | C-8 | Reconnect with backoff | After a broker disconnect, the EMS reconnects with an exponential or otherwise capped backoff policy. | Reconnect storms avoided; subscriptions re-established before resuming publishes. | All
Connection | C-9 | Behavior when telemetry cannot be published | When the EMS cannot publish (broker unreachable, TLS error), it buffers telemetry locally rather than dropping it silently. | Buffered telemetry replays per the Backfill module (see BF-1). | All
Topic addressing | T-1 | siteId format | Site identifiers are prefixed si_ followed by six lowercase alphanumeric characters (e.g. si_qcf9gn). | Every siteId used in publish or subscribe topics matches ^si_[a-z0-9]{6}$. | All
Topic addressing | T-2 | gatewayId format | Gateway identifiers are prefixed gw_ followed by six lowercase alphanumeric characters. | Every gatewayId matches ^gw_[a-z0-9]{6}$. | All
Topic addressing | T-3 | Publish topic patterns per channel | EMS publishes only on the schema-defined topics: dt/{siteId}/{gatewayId}/{metric}/{lifetime¦energy/{window}¦power¦state}, dt/{siteId}/{gatewayId}/{curtailment¦irradiation¦alert¦alert/active¦frequency}, ack-cmd/{siteId}. | No publishes to topics outside this list. | All
Topic addressing | T-4 | Subscribe topic patterns per channel | EMS subscribes only to cmd/{siteId}/battery/power, cmd/{siteId}/battery/fcr (FCR integrators only), and ack-dt/{siteId}/{gatewayId}. Wildcards permitted as alternative. | Documented subscriptions match the list above. | All
Topic addressing | T-5 | res_topic namespace | res_topic on every received command points back to the same site. AWS IoT Core enforces topic scoping at the broker layer. | Publish to res_topic succeeds for legitimate commands; foreign-site attempts rejected by broker. | All
Topic addressing | T-6 | ack-cmd and ack-dt namespaces | Command responses are published on ack-cmd/{siteId}. Telemetry feedback is received on ack-dt/{siteId}/{gatewayId}. | EMS uses the correct namespace for each direction. | All
Topic addressing | T-7 | ack-dt topic shape | Telemetry feedback arrives on ack-dt/{siteId}/{gatewayId} exactly. No /telemetry suffix. | EMS subscribes to ack-dt/{siteId}/{gatewayId}. | All
Topic addressing | T-8 | Hot-standby acknowledgement | In hot-standby, only the active gateway acks commands and executes schedules. The standby gateway is subscribed but stays silent until promoted. Primary/standby coordination is the EMS partner's responsibility. | Under hot-standby, exactly one CommandResponse per command, and exactly one gateway executes the schedule. | All
Message envelope | E-1 | schema_version present on every message | Every published payload includes schema_version, including AlertEvent and AlertState. | schema_version present on every message the EMS emits. | All
Message envelope | E-2 | schema_version value | schema_version is "2.6.0" for every message emitted under this revision. Tensor Cloud remains backwards-compatible with older revisions. | Every emitted schema_version is "2.6.0". | All
Message envelope | E-3 | message_id format | Every message_id matches ^msg_[0-9a-f]{8}-[0-9a-f]{4}-[0-9a-f]{4}-[0-9a-f]{4}-[0-9a-f]{12}$. | All generated message_id values pass the regex. | All
Message envelope | E-4 | command_id correlation | Every CommandResponse carries command_id equal to the originating command's message_id. Exception: an unparseable command (MESSAGE_MALFORMED) has no recoverable message_id, so the response carries the sentinel command_id "unknown". | Every response's command_id matches a command's message_id; for a deliberately malformed (non-JSON) command, the response carries command_id "unknown". | All
Message envelope | E-5 | Timestamps | All *_ts fields are ISO-8601 timestamps with a timezone offset (e.g. 2024-01-05T00:00:00.000+09:00). | Every emitted timestamp parses as ISO-8601 with offset. | All
Message envelope | E-6 | additionalProperties policy | Schema allows unknown fields on every message family for forward-compatibility. EMS still emits only schema-defined fields; receivers tolerate additions. | Every emitted payload contains only schema-defined fields. Parser tolerates unknown fields without crashing. | All
Battery telemetry | BT-1 | Power telemetry shape | Battery power telemetry publishes on dt/{siteId}/{gatewayId}/{metric}/power with a PowerInstant payload. | Publishes validate against the schema; metric is from the battery subset of the metric enum. | All
Battery telemetry | BT-2 | State telemetry shape | Battery state telemetry (SoC, etc.) publishes on dt/{siteId}/{gatewayId}/{metric}/state with a BatteryStateValue payload. | Publishes validate against the schema. | All
Battery telemetry | BT-3 | Telemetry cadence | Telemetry is published at the cadence documented by Tensor (typically minutely for power and state). | Observed cadence matches documented expectation across a representative window of at least 1 hour of continuous operation. | All
Battery telemetry | BT-4 | Telemetry freshness on reconnect | After a disconnect, the EMS prioritizes the latest sample over backfilled history when publishing resumes. | First message published after reconnect carries the freshest sample, not the oldest buffered one. | All
Battery telemetry | BT-5 | Telemetry feedback consumption | EMS subscribes to ack-dt/{siteId}/{gatewayId} and reacts to TelemetryFeedback messages. | EMS handles status: ok and status: error feedback. | All
Battery telemetry | BT-6 | Telemetry feedback retry behavior | EMS has a documented retry / drop policy in response to telemetry feedback errors. | EMS behavior matches the documented policy. | All
Battery telemetry | BT-7 | TelemetryFeedback conditional fields | TelemetryFeedback carries code and detail when status is error, omits code, detail and topic when ok. Schema enforces via if/then/else. | EMS-side parser handles both shapes (no crash, no silent drop) and treats code/detail/topic on ok as a protocol violation. | All
Battery telemetry | BT-8 | Malformed telemetry feedback | When Tensor Cloud cannot parse a telemetry message it acks with code: MESSAGE_MALFORMED, correlation_id: unknown (message_id unrecoverable) and a topic naming the channel. correlation_id is not constrained to the msg_ UUID pattern. | EMS parser accepts correlation_id: unknown without rejecting or dropping the feedback, and surfaces topic so an operator can identify which published message was rejected. | All
Energy reporting | EN-1 | At least one energy reading stream per required metric | For each energy-flow metric required by the project type, EMS emits either a windowed stream, a lifetime counter, or both. | Every required energy-flow metric has at least one active stream across at least 1 hour of continuous operation. | All
Energy reporting | EN-2 | Lifetime counter monotonicity | Values on dt/{siteId}/{gatewayId}/{metric}/lifetime never decrease across messages (except for documented counter-reset events). | Monotonic non-decreasing across a representative observation window. | All
Energy reporting | EN-3 | Lifetime counter units | Lifetime payloads use kWh per EnergyLifetime schema. | All lifetime values are kWh. | All
Energy reporting | EN-4 | Windowed bucket boundaries | For dt/{siteId}/{gatewayId}/{metric}/energy/{window}, start_ts and end_ts boundaries match the {window} parameter, an ISO-8601 duration (PT5M, PT30M, PT1H, etc.). | Every windowed payload's start_ts/end_ts matches the window length implied by the topic. | All
Energy reporting | EN-5 | Late-arrival policy | EMS publishes windowed energy values only after the window has closed. Tensor Cloud has no late-arrival cutoff. | EMS publishes windowed values strictly after window close. Late-arriving samples are still published rather than dropped. | All
Alerts | A-1 | alertEvent emission | Transient alert events publish on dt/{siteId}/{gatewayId}/alert conforming to AlertEvent. | Every emitted code is a member of AlertCode. | All
Alerts | A-2 | alertState clearing semantics | When an alert resolves, the next alertState snapshot omits it. alertState is a periodic full snapshot (at least every 10 minutes, and at startup). | After a resolved alert, the next alertState does not include the resolved alert. | All
Alerts | A-4 | AlertCode enumeration coverage | All codes emitted by the EMS appear in the schema's AlertCode enum. | No proprietary alert codes are emitted on these topics. | All
Backfill | BF-1 | Reconnect replay ordering | After a network outage, the EMS resumes publishing live samples first. Only when no live sample is waiting does it replay buffered history. | Live samples ahead of backfill; backfill yields to fresh live samples whenever they arrive. | All
Backfill | BF-2 | Maximum backlog age | EMS retains telemetry locally for up to 7 days. Older buffered samples are dropped or summarized. | EMS drops or summarizes buffered samples older than 7 days; samples younger than 7 days are replayed. | All
Backfill | BF-3 | Duplicate handling on reconnect | When the EMS resends a sample, it reuses the same message_id as the original. Tensor Cloud dedups on message_id. | Every resend carries the same message_id as its first publish attempt. | All
Arbitrage | AR-1 | Receive power command | EMS receives a representative BatteryPowerCommand. | Message delivered, parsed without error. | Arbitrage
Arbitrage | AR-2 | Command shape per schema | Payload contains schema_version, message_id, issue_ts, res_topic, and a control object with priority (optional) and schedule (required). | Payload validates against BatteryPowerCommand. | Arbitrage
Arbitrage | AR-3 | ack-cmd success response | EMS publishes on ack-cmd/{siteId} with status: ok, command_id equal to the command's message_id, and schema_version: 2.6.0. | Response validates against CommandResponse; errors is absent. | Arbitrage
Arbitrage | AR-4 | ack-cmd error response shape | On rejecting a command, EMS publishes status: error with an errors array. Each error has code (from ErrorCode) and detail. | Response uses detail for each error; every code is from ErrorCode. | Arbitrage
Arbitrage | AR-5 | errors conditional on status | errors array present (>= 1 item) when status is error; absent when status is ok. Schema enforces via if/then/else. | errors present on error; errors absent on ok. | Arbitrage
Arbitrage | AR-6 | ErrorCode mapping | EMS uses the documented ErrorCode for each failure class: MESSAGE_MALFORMED, MISSING_FIELD, TYPE_MISMATCH, FIELD_OUT_OF_RANGE, TIME_WINDOW_INVALID, EXPIRED, DUPLICATE, RESOURCE_UNAVAILABLE, INTERNAL_ERROR. | Same failure class always produces the same code across runs. | Arbitrage
Arbitrage | AR-7 | Schedule gaps | Send a schedule with a time gap between intervals. During the gap, EMS falls back to any previously valid command. If none, power_kw = 0 (standby). | Gap behavior matches: fallback to previous schedule, then standby. | Arbitrage
Arbitrage | AR-8 | Overlaps within a command | Send a schedule whose intervals overlap each other. | EMS rejects with a documented ErrorCode and field_path: control.schedule. | Arbitrage
Arbitrage | AR-9 | Empty schedule | Send a command with an empty schedule array. Schema enforces minItems: 1. | EMS rejects with a documented ErrorCode and field_path: control.schedule. | Arbitrage
Arbitrage | AR-10 | Priority and issue_ts tie-breaking | Different priority: higher wins. Same priority: later issue_ts wins. Same priority and issue_ts: last-received wins. | EMS executes the winning command for each tie-break scenario and acknowledges all commands. | Arbitrage
Arbitrage | AR-11 | Stale-schedule rejection | Send a command whose schedule's last interval end_ts is in the past. | EMS rejects with a documented ErrorCode. Old issue_ts alone is not a rejection reason. | Arbitrage
Arbitrage | AR-12 | Per-slot supersession | Send a command that overlaps only part of an in-progress schedule. The new command replaces existing schedule only for overlapping slots. | EMS uses new command's setpoints for overlapping slots; continues older command for non-overlapping slots. | Arbitrage
Arbitrage | AR-13 | Mid-slot command (immediate execution) | Send a command whose first interval has a start_ts in the past and an end_ts in the future - the covered slot has already started. | EMS accepts the command and applies the active interval's setpoint immediately, without waiting for a future start time. Only a schedule whose final end_ts is also in the past is rejected as stale (see AR-11). | Arbitrage
Arbitrage | AR-14 | No schedule (standby fallback) | Reach a point in time that no command covers and to which no previously valid command applies. | EMS stops the battery and holds power_kw = 0 (standby), neither charging nor discharging, until a command covering that time arrives. | Arbitrage
FCR | FC-1 | Receive FCR command | EMS receives a representative BatteryFcrCommand. | Message delivered, parsed without error. | FCR
FCR | FC-2 | action defaults to execute | When action is absent on a schedule item, EMS treats it as execute. | Matches the schema's default. | FCR
FCR | FC-3 | capacity_kw required for execute | For action: execute (the default), EMS requires capacity_kw and rejects items missing it. Schema enforces via if/then/else. | EMS rejects with a documented ErrorCode and field_path pointing at the offending item. | FCR
FCR | FC-4 | capacity_kw forbidden on cancel | For action: cancel, capacity_kw is forbidden on schedule items. Schema enforces via if/then/else. | EMS rejects a cancel command carrying capacity_kw with a documented ErrorCode. | FCR
FCR | FC-5 | FCR Assessment II power telemetry | For every FCR-awarded slot, EMS publishes 1-second-resolution supplied power at 1 Hz on dt/{siteId}/{gatewayId}/{metric}/power (PowerInstant), PT1S-averaged with measurement_ts at the start of each whole second. Metric set matches the TSO registration: meter_export_ac/meter_import_ac (grid-connection-point) or battery_discharge_ac/battery_charge_ac (equipment-point). | Power samples arrive at 1 Hz on the registered metric(s), carry aggregation: average with aggregation_window: PT1S and whole-second measurement_ts, and time-align with the FC-8 frequency samples. | FCR
FCR | FC-7 | FCR baseline composition with arbitrage | Arbitrage and FCR compose: FCR sets capacity, concurrent BatteryPowerCommand shifts baseline. | When both schedules cover the same slot, EMS applies arbitrage value as baseline and uses FCR capacity for frequency response on top. | FCR
FCR | FC-8 | Grid frequency telemetry | For every FCR-awarded slot, EMS publishes grid frequency at 1 Hz on dt/{siteId}/{gatewayId}/frequency (GridFrequency), in Hz, measured at the grid connection point from the live AC waveform to >= 0.0001 Hz resolution, as a PT1S average time-aligned with the 1 Hz power samples. | Frequency samples arrive at 1 Hz, carry unit: Hz and realistic values, and share measurement_ts boundaries with the power samples. | FCR
FCR | FC-9 | Pre-qualification (事前審査) flag | While the EMS operator has the site in FCR pre-qualification (事前審査) test mode, EMS sets pre_qualification: true on every */power and */frequency message, and omits it (or sets false) during normal operation. | In a simulated pre-qualification run, pre_qualification: true is present on all */power and */frequency messages for the test window and absent during normal operation. | FCR
Solar | SO-1 | Irradiation telemetry | EMS publishes on dt/{siteId}/{gatewayId}/irradiation conforming to Irradiation. | Publishes validate against the schema. | AC-link, DC-link with PV
Solar | SO-2 | Irradiation cadence | EMS publishes irradiation at the documented cadence (typically continuous during daylight, paused or zero at night). | Observed cadence matches documented expectation across at least 1 hour of continuous daylight operation. | AC-link, DC-link with PV
Solar | SO-3 | Curtailment reporting | EMS publishes curtailment on dt/{siteId}/{gatewayId}/curtailment conforming to Curtailment. | Publishes validate against the schema; curtailment is reported whenever the inverter is operating below available irradiation. | AC-link, DC-link with PV
Solar | SO-4 | Solar power telemetry metrics | PV-related metrics (solar_to_grid_ac, solar_to_battery_ac etc.) publish on the power topic. | Every PV metric the EMS supports is emitted on dt/{siteId}/{gatewayId}/{metric}/power. | AC-link, DC-link with PV
Solar | SO-5 | inverter_net_output_ac definition | EMS emits inverter_net_output_ac as the total AC-side output of the inverter, equal to inverter_to_load_ac + inverter_to_grid_ac. Values are non-negative. | Emitted values are >= 0 and equal inverter_to_load_ac + inverter_to_grid_ac. | AC-link, DC-link with PV
Solar | SO-6 | Solar DC voltage and current (DC-link) | DC-link integrators publish PV-array DC voltage and current on dt/{siteId}/{gatewayId}/solar conforming to SolarDcElectrical. measurement_value carries voltage (V) and current (A), each value >= 0, as a single aggregate across the whole array measured at the DC link upstream of the inverter. Voltage and current share one measurement_ts and are published at 1-minute resolution. | Publishes validate against the schema; each message carries both voltage and current at a single measurement_ts; cadence is at least once per minute during daylight. AC-link and stand-alone integrators do not publish this channel. | DC-link with PV
Site load | SL-1 | Load power telemetry | EMS publishes load-side power metrics on dt/{siteId}/{gatewayId}/{metric}/power. | Publishes validate against PowerInstant. | AC-link with load
Site load | SL-2 | Load metric naming | EMS uses inverter_to_load_ac, not inverter_to_load_kwh. | Every load-related metric is the canonical name from the metric enum. | AC-link with load
Site load | SL-3 | Grid-charging metric (DC-link) | For DC-link sites where grid charging is possible, EMS emits grid_to_inverter_ac. | Metric is emitted whenever the site can be charged from grid. | DC-link with grid charging
Site load | SL-4 | Grid-charging metric (AC-link) | For AC-link sites where grid charging is possible, EMS emits grid_to_battery_ac. | grid_to_battery_ac is emitted whenever the site can be charged from grid. | AC-link with grid charging
Project-type constraints | PT-S | Standalone metric set | EMS publishes only metrics from the required + permitted set for standalone batteries. | AWS IoT Core enforces topic scoping at the broker layer based on the gateway's certificate; unauthorized metric topics are rejected at connection time. | Standalone
Project-type constraints | PT-AC | AC-link metric set | EMS publishes only AC-link required + permitted metrics; no DC-link-only metrics. | Only AC-link required and permitted metrics appear on any telemetry topic. | AC-link
Project-type constraints | PT-DC | DC-link metric set | EMS publishes only DC-link required + permitted metrics; no AC-link-only metrics. Includes grid_to_inverter_ac when grid charging is possible. | Only DC-link required and permitted metrics appear on any telemetry topic. | DC-link